## Instrumentation Cables
Instrument And Wires List
TAG NO | Controls Notes | P&IDs Notes | Voltage | INTRINSICALLY SAFE | SIGNAL | CONNECTION | Cable Designation | Cable Qty | Conduit | Conduit Branch | IN STOCK CABLES
CBL 811 |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | CUSTOMER DCS - LCP-1 |  | Company | Designation | Size | Conductors | Shield | Voltage | Type | Nom Diameter
CBL 813 |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | CUSTOMER DCS - LCP-1 |  | Dekoron | Dek2C | 16 AWG | 2 C | Yes | 600 V | TC-ER | 0.287
XL-1 |  |  |  | NO | DIGITAL CONTACT | 4 pair shielded | Dek2C | 1 | CUSTOMER MCC - LCP-1 |  | Dekoron | Dek3C | 16 AWG | 3 C | Yes | 600 V | TC-ER | 0.325
XA-1 |  |  |  | NO | DIGITAL CONTACT | … | Dek2C | 1 | CUSTOMER MCC - LCP-1 |  | Dekoron | Dek4C | 16 AWG | 4 C | Yes | 600 V | TC-ER | 0.355
XL-3 |  |  |  | NO | DIGITAL CONTACT | … | Dek2C | 1 | CUSTOMER MCC - LCP-1 |  | Alan Wire | Alan16 | 16 AWG | 1 C | No | 600 V | TFFN oil gas | 0.095
XL-4 |  |  |  | NO | DIGITAL CONTACT | … | Dek2C | 1 | CUSTOMER MCC - LCP-1 |  | Alan Wire | Alan10 | 10 AWG | 1 C | No | 600 V | TC-ER | 0.16
XY-1 |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | CUSTOMER MCC - LCP-1 |  | Alan Wire | Alan6 | 6 AWG | 1 C | No | 600 V | TC-ER
XY-3 |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | CUSTOMER MCC - LCP-1 |  | Advanced Digital Cable | Advanced14 | 14 AWG | 3 C | No | 600 V | TC-ER
XY-4 |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | CUSTOMER MCC - LCP-1 |  | Reynolds | Motor12 | 18 AWG | 12 C | No | 600 V | TC-ER | 0.43
II-1 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | CUSTOMER MCC - LCP-1 |  | Reynolds | Motor12Sh | 18 AWG | 12 C | Yes | 600 V | TC-ER | 0.51
XT-7A |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | CUSTOMER MCC - LCP-1
RUN INTERLOCK |  |  |  | NO | DIGITAL CONTACT | 2 wire shielded | Dek2C | 1 | FROM CUSTOMER - LCP-1
VSH-1 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | FROM CUSTOMER - LCP-1
ZE-1A |  |  |  | YES | 4-20 mA | 3 wire shielded | Dek3C | 1 | GREEN | G2
ZE-1B |  |  |  | YES | 4-20 mA | 3 wire shielded | Dek3C | 1 | GREEN | G1
PCV-201 |  |  |  | YES | 4-20 mA | 2 wire shielded | Dek2C | 1 | GREEN | G2
TCV-201 |  |  |  | YES | 4-20 mA | 2 wire shielded | Dek2C | 1 | GREEN | G2
ZSO-071 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3
ZSC-071 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3
ZSO-151 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3
ZSC-151 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3
ZSO-201 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R4
ZSC-201 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R4 |  |  |  | Minimum required Conduit Size
SV-071 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3 | Conduit | Number of Cables | Sum of Cross Sectional Areas | Rigid Metal Conduit | Liquidtight Flexible Nonmetallic Conduit | Flexible Metal Conduit | Chosen Size
SV-201 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R4 | B1 | 2 | 0 | ½ | 3/8 | 3/8 | 3/4
SV-151 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R3 | B2 | 2 | 0 | ½ | 3/8 | 3/8 | 3/4
SV-075 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | RED | R2 | BLUE | 4 | 0 | ½ | 3/8 | 3/8 | 3/4
PT-1 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R3 | CUSTOMER DCS - LCP-1 | 4 | 0.028353 | ½ | 3/8 | 3/8
PT-3 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R3 | CUSTOMER MCC - LCP-1 | 12 | 0.43068 | 1¼ | 1 1/4 | 3/4
PT-6 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y1 | FROM CUSTOMER - LCP-1 | 3 | 0.078869 | ½ | 1/2 | 3/8
VT-1 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R2 | G1 | 1 | 0.082958 | ½ | 3/8 | 3/8 | 3/4
VT-2 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R1 | G2 | 3 | 0.21234 | ¾ | 3/4 | 1/2 | 3/4
TT-1 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R3 | GREEN | 4 | 0.2953 | 1 | 1 | 1/2 | 1
TT-3 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R5 | R1 | 9 | 0.72835 | 1½ | 1 1/2 | 1 | 1 1/2
TT-4 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R5 | R2 | 3 | 0.078869 | ½ | 1/2 | 3/8 | 3/4
TT-5 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | RED | R3 | R3 | 17 | 0.40852 | 1¼ | 1 1/4 | 3/4 | 1 1/4
TE-8 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | R4 | 6 | 0.042529 | ½ | 3/8 | 3/8 | 3/4
TE-9 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | R5 | 2 | 0.12938 | ¾ | 3/4 | 3/8 | 3/4
TE-10 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | RED | 36 | 1.323 | 2 | 2 | 1 1/2 | 2
TE-11 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | Y1 | 1 | 0.064692 | ½ | 3/8 | 3/8 | 3/4
TE-12 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | Y2 | 2 | 0.12938 | ¾ | 3/4 | 3/8 | 3/4
TE-13 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | Y3 | 16 | 0.11341 | ½ | 1/2 | 3/8 | 3/4
TE-14 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | Y4 | 17 | 0.40852 | 1¼ | 1 1/4 | 3/4 | 1 1/4
TE-15 |  |  |  | NO | 4-20 mA | 3 wire shielded | Dek3C | 1 | RED | R1 | Y5 | 9 | 0.1214 | ½ | 1/2 | 3/8 | 3/4
LSHH-1 N.C |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3 | Y6 | 7 | 0.10722 | ½ | 1/2 | 3/8 | 3/4
LSHH-1 N.O |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3 | YELLOW | 53 | 1.0093 | 2 | 2 | 1 1/4 | 2
LSHH-2 N.C |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
LSHH-2 N.O |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
LSHH-1 PW |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
LSLL-1 PW |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
LSHH-2 PW |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
LSLL-2 PW |  |  |  | NO | DIGITAL CONTACT | 2 wire | Alan16 | 2 | YELLOW | Y3
ZSO-073 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y6
ZSC-073 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y6
ZSO-074 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
ZSC-074 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
ZS0-072 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
ZSC-072 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
SV-022 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y5
SV-021 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y5
SV-024 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y5
SV-023 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y5
SV-073 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y6
SV-074 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
SV-072 |  |  |  | NO | 4-20 mA | 2 wire | Alan16 | 2 | YELLOW | Y4
PT-2 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y4
PT-4 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y4
PT-5 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | R3
PT-7 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y4
PT-8 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y4
LT-1 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y2
LT-2 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y2
TT-2 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y5
TT-6 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y6
TT-7 |  |  |  | NO | 4-20 mA | 2 wire shielded | Dek2C | 1 | YELLOW | Y4
AH 809 |  |  |  | NO | ALARM | 2 wire | Alan16 | 2
HTR 1 | [5 empty] | 2 wire | Alan14 | 2 | BLUE | B1
HTR 2 | [5 empty] | 2 wire | Alan14 | 2 | BLUE | B2

## Cables Tables
NEC Table 310.15(B)(2)(a) |  |  |  |  | Number of Conductors |  | NEC Table 310.16 Cable Ampacity for Raceway / Conduit | [6 empty] | NEC Table 250.122 Minimum size equipment grounding conductors EGCs |  |  | NEMA Preferred HP ratings for Motors | [5 empty] | NEC Table 310.17
Ambient Temperature | Temperature Rating of Conductor |  |  | Ambient Temperature | Number of Conductors | Percent of Values in Table 310.15(B)(16) through Table 310.15(B)(19) as Adjusted for Ambient Temperature if Necessary | Size | Copper Conductors |  |  | Aluminum Conductors |  |  | OCPD Rating (Amperes) | Copper (AWG or kcmil) | Aluminum or Copper-Clad Aluminum (AWG or kcmil) | HP_Col1 | HP_Col2 | HP_Col3 | HP_Col4 | HP_Col5 | HP_Col6 | Size | Copper Conductors |  |  | Aluminum Conductors
(°C) | 60°C | 75°C | 90°C | (°F) | 4—6 | 80 | AWG/kcmil | 60°C | 75°C | 90°C | 60°C | 75°C | 90°C | 6000 | 800 kcmil | 1250 kcmil | 1/2 | 10 | 75 | 400 | 1250 | 4000 | AWG/kcmil | 60°C | 75°C | 90°C | 60°C | 75°C | 90°C
10 or less | 1.29 | 1.2 | 1.15 | 50 or less | 7—9 | 70 | 18 AWG | — | — | 14 | — | — | — | 5000 | 700 kcmil | 1250 kcmil | 3/4 | 15 | 100 | 450 | 1500 | 4500 | 18 AWG |  |  | 18
11–15 | 1.22 | 1.15 | 1.12 | 51–59 | 10—20 | 50 | 16 AWG | — | — | 18 | — | — | — | 4000 | 500 kcmil | 750 kcmil | 1 | 20 | 125 | 500 | 1750 | 5000 | 16 AWG |  |  | 24
16–20 | 1.15 | 1.11 | 1.08 | 60–68 | 21—30 | 45 | 14 AWG | 20 | 25 | 30 | — | — | — | 3000 | 400 kcmil | 600 kcmil | 1-1/2 | 25 | 150 | 600 | 2000 | - | 14 AWG | 25 | 30 | 35
21–25 | 1.08 | 1.05 | 1.04 | 69–77 | 31—40 | 40 | 12 AWG | 25 | 30 | 35 | 20 | 25 | 30 | 2500 | 350 kcmil | 600 kcmil | 2 | 30 | 200 | 700 | 2250 | - | 12 AWG | 30 | 35 | 40 | 25 | 30 | 35
26–30 | 1 | 1 | 1 | 78–86 | 41 and above | 35 | 10 AWG | 30 | 35 | 40 | 25 | 30 | 35 | 2000 | 250 kcmil | 400 kcmil | 3 | 40 | 250 | 800 | 2500 | - | 10 AWG | 40 | 50 | 55 | 35 | 40 | 45
31–35 | 0.91 | 0.94 | 0.96 | 87–95 |  |  | 8 AWG | 40 | 50 | 55 | 35 | 40 | 45 | 1600 | 4/0 AWG | 350 kcmil | 5 | 50 | 300 | 900 | 3000 | - | 8 AWG | 60 | 70 | 80 | 45 | 55 | 60
36–40 | 0.82 | 0.88 | 0.91 | 96–104 |  |  | 6 AWG | 55 | 65 | 75 | 40 | 50 | 60 | 1200 | 3/0 AWG | 250 kcmil | 7-1/2 | 60 | 350 | 1000 | 3500 | - | 6 AWG | 80 | 95 | 105 | 60 | 75 | 85
41–45 | 0.71 | 0.82 | 0.87 | 105–113 |  |  | 4 AWG | 70 | 85 | 95 | 55 | 65 | 75 | 1000 | 2/0 AWG | 4/0 AWG | [6 empty] | 4 AWG | 105 | 125 | 140 | 80 | 100 | 115
46–50 | 0.58 | 0.75 | 0.82 | 114–122 |  |  | 3 AWG | 85 | 100 | 110 | 65 | 75 | 85 | 800 | 1/0 AWG | 3/0 AWG | [6 empty] | 3 AWG | 120 | 145 | 165 | 95 | 115 | 130
51–55 | 0.41 | 0.67 | 0.76 | 123–131 | Rating | Common Insulation Types | 2 AWG | 95 | 115 | 130 | 75 | 90 | 100 | 600 | 1 AWG | 2/0 AWG | NEMA Preferred RPM ratings for Motors | [5 empty] | 2 AWG | 140 | 170 | 190 | 110 | 135 | 150
56–60 | — | 0.58 | 0.71 | 132–140 | 60°C | TW, UF | 1 AWG | 110 | 130 | 150 | 85 | 100 | 115 | 500 | 2 AWG | 1/0 AWG | Speed_Col1 | Speed_Col2 | Speed_Col3 | Speed_Col4 |  |  | 1 AWG | 165 | 195 | 220 | 130 | 155 | 175
61–65 | — | 0.47 | 0.65 | 141–149 | 75°C | THW, THWN, RHW, XHHW (wet) | 1/0 AWG | 125 | 150 | 170 | 100 | 120 | 135 | 400 | 3 AWG | 1 AWG | 300 | 650 | 1750 | 5000 |  |  | 1/0 AWG | 195 | 230 | 260 | 150 | 180 | 205
66–70 | — | 0.33 | 0.58 | 150–158 | 90°C | THHN, THWN-2, XHHW-2, USE-2 | 2/0 AWG | 145 | 175 | 195 | 115 | 135 | 150 | 300 | 4 AWG | 2 AWG | 400 | 850 | 2500 | 7000 |  |  | 2/0 AWG | 225 | 265 | 300 | 175 | 210 | 235
71–75 | — | — | 0.5 | 159–167 |  |  | 3/0 AWG | 165 | 200 | 225 | 130 | 155 | 175 | 200 | 6 AWG | 4 AWG | 500 | 1150 | 3500 | 10000 |  |  | 3/0 AWG | 260 | 310 | 350 | 200 | 240 | 270
76–80 | — | — | 0.41 | 168–176 |  |  | 4/0 AWG | 195 | 230 | 260 | 150 | 180 | 205 | 100 | 8 AWG | 6 AWG | [6 empty] | 4/0 AWG | 300 | 360 | 405 | 235 | 280 | 315
81–85 | — | — | 0.29 | 177–185 |  |  | 250 kcmil | 215 | 255 | 290 | 170 | 205 | 230 | 60 | 10 AWG | 8 AWG | [6 empty] | 250 kcmil | 340 | 405 | 455 | 265 | 315 | 355
[7 empty] | 300 kcmil | 240 | 285 | 320 | 190 | 230 | 255 | 20 | 12 AWG | 10 AWG | [6 empty] | 300 kcmil | 375 | 445 | 500 | 290 | 350 | 395
[7 empty] | 350 kcmil | 260 | 310 | 350 | 210 | 250 | 280 | 15 | 14 AWG | 12 AWG | [6 empty] | 350 kcmil | 420 | 505 | 570 | 330 | 395 | 445
[7 empty] | 400 kcmil | 280 | 335 | 380 | 225 | 270 | 305 | [9 empty] | 400 kcmil | 455 | 545 | 615 | 355 | 425 | 480
[7 empty] | 500 kcmil | 320 | 380 | 430 | 260 | 310 | 350 | [9 empty] | 500 kcmil | 515 | 620 | 700 | 405 | 485 | 545
[7 empty] | 600 kcmil | 355 | 420 | 475 | 285 | 340 | 385 | [9 empty] | 600 kcmil | 575 | 690 | 780 | 455 | 545 | 615
[7 empty] | 700 kcmil | 385 | 460 | 520 | 310 | 375 | 425 | [9 empty] | 700 kcmil | 630 | 755 | 850 | 500 | 595 | 670
[7 empty] | 750 kcmil | 400 | 475 | 535 | 320 | 385 | 435 | [9 empty] | 750 kcmil | 655 | 785 | 885 | 515 | 620 | 700
[7 empty] | 800 kcmil | 410 | 490 | 555 | 330 | 395 | 445 | [9 empty] | 800 kcmil | 680 | 815 | 920 | 535 | 645 | 725
[7 empty] | 900 kcmil | 435 | 520 | 585 | 355 | 425 | 480 | [9 empty] | 900 kcmil | 730 | 870 | 980 | 580 | 700 | 790
[7 empty] | 1000 kcmil | 455 | 545 | 615 | 375 | 445 | 500 | [9 empty] | 1000 kcmil | 780 | 935 | 1055 | 625 | 750 | 845
[7 empty] | 1250 kcmil | 495 | 590 | 665 | 405 | 485 | 545 | [9 empty] | 1250 kcmil | 890 | 1065 | 1200 | 710 | 855 | 965
[7 empty] | 1500 kcmil | 525 | 625 | 705 | 435 | 520 | 585 | [9 empty] | 1500 kcmil | 980 | 1175 | 1325 | 795 | 950 | 1070
[7 empty] | 1750 kcmil | 545 | 650 | 735 | 455 | 545 | 615 | [9 empty] | 1750 kcmil | 1070 | 1280 | 1445 | 875 | 1050 | 1185
[7 empty] | 2000 kcmil | 555 | 665 | 750 | 470 | 560 | 630 | [9 empty] | 2000 kcmil | 1155 | 1385 | 1560 | 960 | 1150 | 1295

## Conduit Fittings
Conduit BOM |  |  |  |  | BILL OF MATERIAL | [6 empty] | Conduit Planning
Size | Part | BOM Qty | EPICOR P/N | EPICOR DESCRIPTION | Number | ASM | Mtl Seq | Part | Qty / Parent | UOM | Desc | Size | Tag | Transcribed Contents
#18 AWG | Cable | 30 | 241000309 | MOTOR RTD CABLE, AWG 18, 600 VOLT, LAPP-25 COND | 12 | 68 | 120 | 50110023 | 1 | EA | 1" MEYERS HUB | 1 | GN | MH, LB, TB, 90, X, T
1 1/4" -> 3/4" | RD | 2 | 241000201 | 1-1/4" X 3/4" RE BUSHING | 29 | 68 | 290 | 50110125 | 4 | EA | 1" X 3/4" RE BUSHING | 1-1/4 | R3 | RD, T, down T,T,T,T,T, 90, X
1" | 90° | 1 | 241000125 | 1" 90 DEG. PULL ELB FEM / FEM NON HAZ LOC | 11 | 68 | 110 | 50110860 | 1 | EA | 3/4" MEYERS HUB | 1-1/4 | Y4 | RD, T, d, T, X, X, X, X, X
1" | LB | 1 | 241000118 | 1" MALL LB COND BODY | 7 | 68 | 70 | 50111204 | 4 | EA | COND BODY, MALL, LB, 1/2" | 2 | Red | MH, LB, TB, 90, X, 90, X, X, T, T, 90
1" | MH | 1 | 50110023 | 1" MEYERS HUB | 26 | 68 | 260 | 50111400 | 6 | EA | COND BODY, MALL X, 1-1/4" | 2 | YW | MH, LB, X, LR, T,T,T,X,X
1" | T | 1 | 241000185 | COND BODY, MALL, T, 1" | 15 | 68 | 150 | 50111404 | 15 | EA | COND BODY, MALL T, 3/4" | 3/4 | B1
1" | TB | 1 | 241000122 | 1" MALL TB CONDUIT BODY | 14 | 68 | 140 | 50112048 | 2 | EA | SEAL OFF, MALL, EYS, 3/4" | 3/4 | B2
1" | X | 1 | 241000199 | 1" MALL X CONDUIT BODY | 24 | 68 | 240 | 50112205 | 8 | EA | COND BODY, MALL, X, 3/4", CLIP | 3/4 | BL | MH, LB, TB, ELB, X, X
1" -> 3/4" | RD | 4 | 50110125 | 1" X 3/4" RE BUSHING | 20 | 68 | 200 | 50112229 | 2 | EA | 3/4" MALL TB COND BODY | 3/4 | G1 | RD, 90°, C
1/2" | LB | 4 | 50111204 | COND BODY, MALL, LB, 1/2" | 5 | 68 | 50 | 50112244 | 1 | EA | 3/4" MALE / FEM 90 DEG SHORT ELB HAZ LOC | 3/4 | G2 | RD, X, T, X, LB, TB, UNION90, SEAL, UNION90, SEAL, T, 90, T W DRAIN, C
1-1/4" | 90° | 1 | 241000126 | COND BODY, MALL, LB, 1-1/4" | 18 | 68 | 180 | 241000071 | 2 | EA | COND BODY, MALL, T, 2" | 3/4 | R1 | RD, T
1-1/4" | T | 9 | 241000179 | COND BODY, MALL, T, 1-1/4" | 22 | 68 | 220 | 241000072 | 1 | EA | 2" MALL TB COND BODY | 3/4 | R2 | RD, T LB
1-1/4" | X | 6 | 50111400 | COND BODY, MALL X, 1-1/4" | 13 | 68 | 130 | 241000082 | 2 | EA | MEYERS HUB, 2" | 3/4 | R4 | RD, T
2" | LB | 5 | 241000198 | COND BODY, MALL, LB, 2" | 1 | 68 | 10 | 241000094 | 4 | EA | PULL ELBOW, NON HAZ LOC, 90 DEG. MALE / FEM, 3/4" | 3/4 | R5 | RD, T, down TT4 T, up TT3 T
2" | LR | 1 | 241000101 | COND BODY, MALL, LR, 2" | 27 | 68 | 270 | 241000100 | 6 | EA | 2" MALL X COND BODY | 3/4 | Y1 | RD
2" | MH | 2 | 241000082 | MEYERS HUB, 2" | 10 | 68 | 100 | 241000101 | 1 | EA | COND BODY, MALL, LR, 2" | 3/4 | Y2 | RD, T, X
2" | T | 2 | 241000071 | COND BODY, MALL, T, 2" | 23 | 68 | 230 | 241000109 | 2 | EA | UNION, MALL, HAZ LOC, 90, UNL, 3/4" | 3/4 | Y3 | RD, T, T, T, 90, LB
2" | TB | 1 | 241000072 | 2" MALL TB COND BODY | 4 | 68 | 40 | 241000116 | 2 | EA | 3/4" MALL C COND BODY, CLIP | 3/4 | Y5 | RD, X, X, RD -> 1/2" LB, 1/2" LB, 1/2" LB, 1/2" LB
2" | X | 6 | 241000100 | 2" MALL X COND BODY | 19 | 68 | 190 | 241000117 | 16 | EA | DRAIN BREATHER, 3/4" | 3/4 | Y6 | RD, T, 90, X
2" -> 1 1/4" | RD | 2 | 241000200 | RE BUSH, 2" X 1-1/4" | 8 | 68 | 80 | 241000118 | 1 | EA | 1" MALL LB COND BODY
2" -> 3/4" | RD | 15 | 241000194 | RE BUSH, 2" X 3/4" | 21 | 68 | 210 | 241000122 | 1 | EA | 1" MALL TB CONDUIT BODY
3/4" | 90° | 4 | 241000094 | PULL ELBOW, NON HAZ LOC, 90 DEG. MALE / FEM, 3/4" | 2 | 68 | 20 | 241000125 | 1 | EA | 1" 90 DEG. PULL ELB FEM / FEM NON HAZ LOC
3/4" | C | 2 | 241000116 | 3/4" MALL C COND BODY, CLIP | 3 | 68 | 30 | 241000126 | 1 | EA | COND BODY, MALL, LB, 1-1/4"
3/4" | Drain | 16 | 241000117 | DRAIN BREATHER, 3/4" | 17 | 68 | 170 | 241000179 | 9 | EA | COND BODY, MALL, T, 1-1/4"
3/4" | ELB | 1 | 50112244 | 3/4" MALE / FEM 90 DEG SHORT ELB HAZ LOC | 16 | 68 | 160 | 241000185 | 1 | EA | COND BODY, MALL, T, 1"
3/4" | LB | 4 | 241000187 | COND BODY, MALL, LB, 3/4" | 6 | 68 | 60 | 241000187 | 4 | EA | COND BODY, MALL, LB, 3/4"
3/4" | MH | 1 | 50110860 | 3/4" MEYERS HUB | 28 | 68 | 280 | 241000194 | 15 | EA | RE BUSH, 2" X 3/4"
3/4" | Seal | 2 | 50112048 | SEAL OFF, MALL, EYS, 3/4" | 9 | 68 | 90 | 241000198 | 5 | EA | COND BODY, MALL, LB, 2"
3/4" | T | 15 | 50111404 | COND BODY, MALL T, 3/4" | 25 | 68 | 250 | 241000199 | 1 | EA | 1" MALL X CONDUIT BODY
3/4" | TB | 2 | 50112229 | 3/4" MALL TB COND BODY | 30 | 68 | 300 | 241000200 | 2 | EA | RE BUSH, 2" X 1-1/4"
3/4" | Union 90 | 2 | 241000109 | UNION, MALL, HAZ LOC, 90, UNL, 3/4" | 31 | 68 | 310 | 241000201 | 2 | EA | 1-1/4" X 3/4" RE BUSHING
3/4" | X | 8 | 50112205 | COND BODY, MALL, X, 3/4", CLIP | 32 | 68 | 320 | 241000309 | 30 | FT | MOTOR RTD CABLE, AWG 18, 600 VOLT, LAPP-25 COND
Conduit Planning
Size | Tag | Transcribed Contents
1 | GN | MH, LB, TB, 90, X, T
1-1/4 | R3 | RD, T, down T,T,T,T,T, 90, X
1-1/4 | Y4 | RD, T, d, T, X, X, X, X, X
2 | Red | MH, LB, TB, 90, X, 90, X, X, T, T, 90
2 | YW | MH, LB, X, LR, T,T,T,X,X
3/4 | B1
3/4 | B2
3/4 | BL | MH, LB, TB, ELB, X, X
3/4 | G1 | RD, 90°, C
3/4 | G2 | RD, X, T, X, LB, TB, UNION90, SEAL, UNION90, SEAL, T, 90, T W DRAIN, C
3/4 | R1 | RD, T
3/4 | R2 | RD, T LB
3/4 | R4 | RD, T
3/4 | R5 | RD, T, down TT4 T, up TT3 T
3/4 | Y1 | RD
3/4 | Y2 | RD, T, X
3/4 | Y3 | RD, T, T, T, 90, LB
3/4 | Y5 | RD, X, X, RD -> 1/2" LB, 1/2" LB, 1/2" LB, 1/2" LB
3/4 | Y6 | RD, T, 90, X

## Conduit Tables
Article 344 - Rigid Metal Conduit | [13 empty] | Chapter 9 Table 2 Radius of Conduit and Tubing Bends
Metric Designator | Trade Size | Over 2 Wires 40% mm² | Over 2 Wires 40% in.² | 1 Wire 60% mm² | 1 Wire 60% in.² | 1 Wire 53% mm² | 1 Wire 53% in.² | 2 Wires 31% mm² | 2 Wires 31% in.² | Nominal Internal Diameter mm | Nominal Internal Diameter in. | Total Area 100% mm² | Total Area 100% in.² | Metric Designator | Trade Size | One Shot/Full Shoe (mm) | One Shot/Full Shoe (in) | Other Bends (mm) | Other Bends (in)
12 | ⅜ | — | — | — | — | — | — | — | — | 16.1 | 0.632 | 204 | 0.314 | 16 | 0.5 | 101.6 | 4 | 101.6 | 4
16 | ½ | 81 | 0.125 | 122 | 0.188 | 107 | 0.166 | 63 | 0.097 | 21 | 0.832 | 204 | 0.314 | 21 | 0.75 | 114.3 | 4.5 | 127 | 5
21 | ¾ | 141 | 0.22 | 212 | 0.328 | 185 | 0.291 | 109 | 0.17 | 21.2 | 0.836 | 353 | 0.549 | 27 | 1 | 146.05 | 5.75 | 152.4 | 6
27 | 1 | 229 | 0.355 | 344 | 0.532 | 302 | 0.47 | 177 | 0.275 | 27 | 1.063 | 573 | 0.887 | 35 | 1.25 | 184.15 | 7.25 | 203.2 | 8
35 | 1¼ | 394 | 0.61 | 533 | 0.826 | 468 | 0.709 | 305 | 0.473 | 35.4 | 1.394 | 981 | 1.526 | 41 | 1.5 | 209.55 | 8.25 | 254 | 10
41 | 1½ | 533 | 0.825 | 800 | 1.243 | 702 | 1.089 | 395 | 0.613 | 41.6 | 1.638 | 1333 | 2.071 | 53 | 2 | 241.3 | 9.5 | 304.8 | 12
53 | 2 | 879 | 1.363 | 1318 | 2.045 | 1157 | 1.806 | 681 | 1.056 | 52.9 | 2.083 | 2198 | 3.409 | 63 | 2.5 | 266.7 | 10.5 | 381 | 15
63 | 2½ | 1255 | 1.946 | 1882 | 2.918 | 1654 | 2.563 | 974 | 1.51 | 63.1 | 2.484 | 3129 | 4.866 | 78 | 3 | 330.2 | 13 | 457.2 | 18
78 | 3 | 1936 | 3.004 | 2904 | 4.509 | 2553 | 3.974 | 1503 | 2.34 | 78.5 | 3.09 | 4844 | 7.499 | 91 | 3.5 | 381 | 15 | 533.4 | 21
91 | 3½ | 2584 | 4.004 | 3877 | 6.006 | 3414 | 5.294 | 2000 | 3.099 | 90.7 | 3.57 | 6460 | 10.01 | 103 | 4 | 406.4 | 16 | 609.6 | 24
103 | 4 | 3326 | 5.153 | 4990 | 7.728 | 4396 | 6.828 | 2578 | 3.994 | 102.9 | 4.053 | 8316 | 12.882 | 129 | 5 | 609.6 | 24 | 762 | 30
129 | 5 | 5220 | 8.085 | 7830 | 12.127 | 6896 | 10.667 | 4045 | 6.265 | 129.8 | 5.073 | 13050 | 20.212 | 155 | 6 | 762 | 30 | 914.4 | 36
155 | 6 | 7528 | 11.663 | 11292 | 17.495 | 9975 | 15.454 | 5843 | 9.03 | 154.8 | 6.09 | 18821 | 29.158
Article 356 - Liquidtight Flexible Nonmetallic Conduit
Metric Designator | Trade Size | Over 2 Wires 40% (mm²) | Over 2 Wires 40% (in²) | 60% (mm²) | 60% (in²) | 1 Wire 53% (mm²) | 1 Wire 53% (in²) | 2 Wires 31% (mm²) | 2 Wires 31% (in²) | Nominal ID (mm) | Nominal ID (in) | Total Area 100% (mm²) | Total Area 100% (in²)
12 | 3/8 | 50 | 0.077 | 75 | 0.115 | 66 | 0.102 | 39 | 0.06 | 12.6 | 0.495 | 125 | 0.192
16 | 1/2 | 80 | 0.125 | 121 | 0.187 | 107 | 0.165 | 62 | 0.097 | 16 | 0.63 | 201 | 0.312
21 | 3/4 | 139 | 0.214 | 208 | 0.321 | 184 | 0.283 | 107 | 0.166 | 21 | 0.825 | 346 | 0.535
27 | 1 | 221 | 0.343 | 331 | 0.513 | 292 | 0.453 | 171 | 0.265 | 26.5 | 1.043 | 552 | 0.854
35 | 1 1/4 | 387 | 0.601 | 581 | 0.901 | 513 | 0.796 | 300 | 0.466 | 35.1 | 1.383 | 968 | 1.502
41 | 1 1/2 | 520 | 0.807 | 781 | 1.211 | 690 | 1.07 | 403 | 0.626 | 40.7 | 1.603 | 1301 | 2.018
53 | 2 | 863 | 1.337 | 1294 | 2.006 | 1143 | 1.772 | 669 | 1.036 | 52.4 | 2.063 | 2157 | 3.343
Article 348 - Flexible Metal Conduit
Metric Designator | Trade Size | Over 2 Wires 40% (mm²) | Over 2 Wires 40% (in²) | 60% (mm²) | 60% (in²) | 1 Wire 53% (mm²) | 1 Wire 53% (in²) | 2 Wires 31% (mm²) | 2 Wires 31% (in²) | Nominal ID (mm) | Nominal ID (in) | Total Area 100% (mm²) | Total Area 100% (in²)
12 | 3/8 | 127 | 0.197 | 206 | 0.32 | 182 | 0.283 | 106 | 0.165 | 10.9 | 0.424 | 345 | 0.535
16 | 1/2 | 211 | 0.327 | 316 | 0.49 | 279 | 0.433 | 162 | 0.253 | 15.9 | 0.622 | 527 | 0.817
21 | 3/4 | 330 | 0.511 | 495 | 0.766 | 437 | 0.677 | 253 | 0.396 | 22.4 | 0.882 | 824 | 1.277
27 | 1 | 480 | 0.743 | 720 | 1.111 | 636 | 0.985 | 372 | 0.576 | 29.1 | 1.138 | 1201 | 1.863
35 | 1 1/4 | 843 | 1.307 | 1264 | 1.961 | 1117 | 1.732 | 653 | 1.013 | 39.1 | 1.54 | 2107 | 3.269
41 | 1 1/2 | 1267 | 1.963 | 1900 | 2.945 | 1678 | 2.602 | 980 | 1.522 | 63.5 | 2.5 | 3167 | 4.909
53 | 2 | 1854 | 2.877 | 2736 | 4.241 | 2417 | 3.746 | 1414 | 2.191 | 76.9 | 3.001 | 4560 | 7.068
63 | 2 1/2 | 2483 | 3.848 | 3724 | 5.773 | 3390 | 5.009 | 1921 | 2.983 | 88.9 | 3.5 | 6207 | 9.621
78 | 3 | 3243 | 5.027 | 4861 | 7.54 | 4297 | 6.66 | 2515 | 3.896 | 101.6 | 4 | 8107 | 12.566
Lookup Calculation
Type | Size (AWG/kcmil) | Area mm^2 | Area in^2 | Diameter mm | Diameter in | 0
KF-1, KFF-1 | 10 AWG | 8.194 | 0.0127 | 3.226 | 0.127
KF-1, KFF-1 | 12 AWG | 5.355 | 0.0083 | 2.616 | 0.103
KF-1, KFF-1 | 14 AWG | 3.548 | 0.0055 | 2.134 | 0.084
KF-1, KFF-1 | 16 AWG | 2.387 | 0.0037 | 1.753 | 0.069
KF-1, KFF-1 | 18 AWG | 1.677 | 0.0026 | 1.448 | 0.057
KF-2, KFF-2 | 10 AWG | 8.968 | 0.0139 | 3.378 | 0.133
KF-2, KFF-2 | 12 AWG | 6 | 0.0092 | 2.743 | 0.108
KF-2, KFF-2 | 14 AWG | 4.129 | 0.0064 | 2.286 | 0.09
KF-2, KFF-2 | 16 AWG | 2.889 | 0.0043 | 1.88 | 0.074
KF-2, KFF-2 | 18 AWG | 2 | 0.0031 | 1.575 | 0.062
PF, PGF, PFE, PFF, PTF, PAF, PTFE, PAFF | 14 AWG | 6.452 | 0.01 | 2.87 | 0.113
PF, PGF, PFE, PFF, PTF, PAF, PTFE, PAFF | 16 AWG | 4.839 | 0.0075 | 2.489 | 0.098
PF, PGF, PFE, PFF, PTF, PAF, PTFE, PAFF | 18 AWG | 3.742 | 0.0058 | 2.184 | 0.086
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 2000 kcmil | 1795 | 2.7818 | 47.8 | 1.882
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1750 kcmil | 1598 | 2.4773 | 45.11 | 1.776
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1500 kcmil | 1400 | 2.1695 | 42.21 | 1.662
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1250 kcmil | 1200 | 1.8602 | 39.09 | 1.539
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1000 kcmil | 953.8 | 1.4784 | 34.85 | 1.372
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 900 kcmil | 874.9 | 1.3561 | 33.38 | 1.314
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 800 kcmil | 791.7 | 1.2272 | 31.75 | 1.25
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 750 kcmil | 751.7 | 1.1652 | 30.94 | 1.218
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 700 kcmil | 710.3 | 1.101 | 30.07 | 1.184
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 600 kcmil | 627.7 | 0.9729 | 28.27 | 1.113
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 500 kcmil | 509.7 | 0.7901 | 25.48 | 1.003
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 400 kcmil | 427 | 0.6619 | 23.32 | 0.918
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 350 kcmil | 384.4 | 0.5958 | 22.12 | 0.871
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 300 kcmil | 340.7 | 0.5281 | 20.83 | 0.82
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 250 kcmil | 296.5 | 0.4596 | 19.43 | 0.765
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 4/0 AWG | 239.9 | 0.3718 | 17.48 | 0.688
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 3/0 AWG | 201.1 | 0.3117 | 16 | 0.63
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 2/0 AWG | 169.3 | 0.2624 | 14.68 | 0.578
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1/0 AWG | 143.4 | 0.2223 | 13.51 | 0.532
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 1 AWG | 122.6 | 0.1901 | 12.5 | 0.492
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 2 AWG | 86 | 0.1383 | 10.46 | 0.412
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 3 AWG | 73.16 | 0.1134 | 9.652 | 0.38
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 4 AWG | 62.77 | 0.0973 | 8.941 | 0.352
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 6 AWG | 46.84 | 0.0726 | 7.722 | 0.304
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 8 AWG | 35.87 | 0.0556 | 6.756 | 0.266
RH*, RHW*, XHHW*, XHHW-2*, THHN, THHW, THW, THW-2, TFN, TFFN, THWN, THWN-2, XF, XFF | 10 AWG | 21.48 | 0.0533 | 5.232 | 0.206
RHH*, RHW*, RHW-2* | 12 AWG | 16.77 | 0.026 | 4.623 | 0.182
RHH*, RHW*, RHW-2* | 14 AWG | 13.48 | 0.0209 | 4.14 | 0.163
RHH, RHW, RHW-2 | 2000 kcmil | 2175 | 3.3719 | 52.63 | 2.072
RHH, RHW, RHW-2 | 1750 kcmil | 1959 | 3.0357 | 49.94 | 1.966
RHH, RHW, RHW-2 | 1500 kcmil | 1738 | 2.6938 | 47.04 | 1.852
RHH, RHW, RHW-2 | 1250 kcmil | 1515 | 2.3479 | 43.92 | 1.729
RHH, RHW, RHW-2 | 1000 kcmil | 1143 | 1.7719 | 38.15 | 1.502
RHH, RHW, RHW-2 | 900 kcmil | 1057 | 1.6377 | 36.68 | 1.444
RHH, RHW, RHW-2 | 800 kcmil | 965 | 1.4957 | 35.05 | 1.38
RHH, RHW, RHW-2 | 750 kcmil | 920.8 | 1.4272 | 34.24 | 1.348
RHH, RHW, RHW-2 | 700 kcmil | 874.9 | 1.3561 | 33.88 | 1.334
RHH, RHW, RHW-2 | 600 kcmil | 782.9 | 1.2135 | 31.57 | 1.243
RHH, RHW, RHW-2 | 500 kcmil | 650.5 | 1.0082 | 28.78 | 1.133
RHH, RHW, RHW-2 | 400 kcmil | 556.5 | 0.8626 | 26.62 | 1.048
RHH, RHW, RHW-2 | 350 kcmil | 507.7 | 0.787 | 25.43 | 1.001
RHH, RHW, RHW-2 | 300 kcmil | 457.3 | 0.7088 | 24.13 | 0.95
RHH, RHW, RHW-2 | 250 kcmil | 405.9 | 0.6291 | 22.73 | 0.895
RHH, RHW, RHW-2 | 4/0 AWG | 306.7 | 0.4754 | 19.76 | 0.778
RHH, RHW, RHW-2 | 3/0 AWG | 262.7 | 0.4072 | 18.29 | 0.72
RHH, RHW, RHW-2 | 2/0 AWG | 226.1 | 0.3505 | 16.97 | 0.668
RHH, RHW, RHW-2 | 1/0 AWG | 196.1 | 0.3039 | 15.8 | 0.622
RHH, RHW, RHW-2 | 1 AWG | 171.6 | 0.266 | 14.78 | 0.582
RHH, RHW, RHW-2 | 2 AWG | 112.9 | 0.175 | 11.99 | 0.472
RHH, RHW, RHW-2 | 3 AWG | 98.13 | 0.1521 | 11.18 | 0.44
RHH, RHW, RHW-2 | 4 AWG | 86 | 0.1338 | 10.46 | 0.412
RHH, RHW, RHW-2 | 6 AWG | 67.16 | 0.1041 | 9.246 | 0.364
RHH, RHW, RHW-2 | 8 AWG | 53.87 | 0.0835 | 8.28 | 0.326
RHH, RHW, RHW-2 | 10 AWG | 28.19 | 0.0437 | 5.994 | 0.236
RHH, RHW, RHW-2 | 12 AWG | 22.77 | 0.0353 | 5.385 | 0.212
RHH, RHW, RHW-2 | 14 AWG | 18.9 | 0.0293 | 4.902 | 0.193
RHH-1, TF, TFN, XF, XFF | 18 AWG | 5.161 | 0.0088 | 2.692 | 0.106
SF-1, SFF-1 | 18 AWG | 4.194 | 0.0065 | 2.311 | 0.091
SF-2, SFF-2 | 14 AWG | 11.1 | 0.0172 | 3.759 | 0.148
SF-2, SFF-2 | 16 AWG | 8.968 | 0.0139 | 3.378 | 0.133
SF-2, SFF-2 | 18 AWG | 7.419 | 0.0115 | 3.073 | 0.121
TF, TFN, XF, XFF | 16 AWG | 7.032 | 0.0109 | 2.997 | 0.118
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 2 AWG | 62.77 | 0.0973 | 8.941 | 0.352
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 3 AWG | 51.87 | 0.0804 | 8.128 | 0.32
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 4 AWG | 43.23 | 0.067 | 7.417 | 0.292
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 6 AWG | 30.19 | 0.0468 | 6.138 | 0.244
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 8 AWG | 21.48 | 0.0338 | 5.232 | 0.206
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 10 AWG | 12.52 | 0.0191 | 3.962 | 0.156
TFE, FEP, PFA, PFF, PF, PAF, PEH, PAFH | 12 AWG | 8.839 | 0.0137 | 3.353 | 0.132
TFE, PFA, PFAH, Z | 4/0 AWG | 193.5 | 0.3 | 15.7 | 0.618
TFE, PFA, PFAH, Z | 3/0 AWG | 158.9 | 0.2463 | 14.22 | 0.56
TFE, PFA, PFAH, Z | 2/0 AWG | 130.8 | 0.2027 | 12.9 | 0.508
TFE, PFA, PFAH, Z | 1/0 AWG | 108.1 | 0.1676 | 11.73 | 0.462
TFE, PFAH, PFA | 1 AWG | 90.26 | 0.1399 | 10.72 | 0.422
TFN, TFFN | 16 AWG | 4.645 | 0.0072 | 2.438 | 0.096
TFN, TFFN | 18 AWG | 3.548 | 0.0055 | 2.134 | 0.084
THHN, THWN, THWN-2 | 1000 kcmil | 869.5 | 1.3478 | 33.27 | 1.31
THHN, THWN, THWN-2 | 900 kcmil | 794.3 | 1.2311 | 31.8 | 1.252
THHN, THWN, THWN-2 | 800 kcmil | 715.2 | 1.1085 | 30.18 | 1.188
THHN, THWN, THWN-2 | 750 kcmil | 677.2 | 1.0496 | 29.36 | 1.156
THHN, THWN, THWN-2 | 700 kcmil | 637.9 | 0.9887 | 28.5 | 1.122
THHN, THWN, THWN-2 | 600 kcmil | 559.7 | 0.8676 | 26.7 | 1.051
THHN, THWN, THWN-2 | 500 kcmil | 456.3 | 0.7073 | 24.1 | 0.949
THHN, THWN, THWN-2 | 400 kcmil | 378.3 | 0.5863 | 21.95 | 0.864
THHN, THWN, THWN-2 | 350 kcmil | 338.2 | 0.5242 | 20.75 | 0.817
THHN, THWN, THWN-2 | 300 kcmil | 297.3 | 0.4608 | 19.46 | 0.766
THHN, THWN, THWN-2 | 250 kcmil | 256.1 | 0.397 | 18.06 | 0.711
THHN, THWN, THWN-2 | 4/0 AWG | 208.8 | 0.3237 | 16.31 | 0.642
THHN, THWN, THWN-2 | 3/0 AWG | 172.8 | 0.2679 | 14.83 | 0.584
THHN, THWN, THWN-2 | 2/0 AWG | 143.4 | 0.2233 | 13.51 | 0.539
THHN, THWN, THWN-2 | 1/0 AWG | 119.7 | 0.1855 | 12.34 | 0.486
THHN, THWN, THWN-2 | 1 AWG | 100.8 | 0.1562 | 11.33 | 0.446
THHN, THWN, THWN-2 | 2 AWG | 74.71 | 0.1158 | 9.754 | 0.384
THHN, THWN, THWN-2 | 3 AWG | 62.77 | 0.0973 | 8.941 | 0.352
THHN, THWN, THWN-2 | 4 AWG | 53.16 | 0.0824 | 8.23 | 0.324
THHN, THWN, THWN-2 | 6 AWG | 32.71 | 0.0507 | 6.452 | 0.254
THHN, THWN, THWN-2 | 8 AWG | 23.61 | 0.0366 | 5.486 | 0.216
THHN, THWN, THWN-2 | 10 AWG | 13.61 | 0.0211 | 4.166 | 0.164
THHN, THWN, THWN-2 | 12 AWG | 8.581 | 0.0133 | 3.302 | 0.13
THHN, THWN, THWN-2 | 14 AWG | 6.258 | 0.0097 | 2.819 | 0.111
TW, THHW, THW, THW-2 | 8 AWG | 28.19 | 0.0437 | 5.994 | 0.236
TW, THHW, THW, THW-2 | 10 AWG | 15.68 | 0.0243 | 4.47 | 0.176
TW, THHW, THW, THW-2 | 12 AWG | 11.68 | 0.0181 | 3.861 | 0.152
TW, XF, XFF, THHW, THW, THW-2 | 14 AWG | 8.968 | 0.0139 | 3.378 | 0.133
XHHW, XHHW-2, XHH | 2000 kcmil | 1682 | 2.6073 | 46.28 | 1.822
XHHW, XHHW-2, XHH | 1750 kcmil | 1492 | 2.3127 | 43.59 | 1.716
XHHW, XHHW-2, XHH | 1500 kcmil | 1300 | 2.0156 | 40.69 | 1.602
XHHW, XHHW-2, XHH | 1250 kcmil | 1108 | 1.718 | 37.57 | 1.479
XHHW, XHHW-2, XHH | 1000 kcmil | 872.2 | 1.3519 | 33.32 | 1.312
XHHW, XHHW-2, XHH | 900 kcmil | 796.8 | 1.2351 | 31.85 | 1.254
XHHW, XHHW-2, XHH | 800 kcmil | 717.5 | 1.1122 | 30.23 | 1.19
XHHW, XHHW-2, XHH | 750 kcmil | 679.5 | 1.0532 | 29.41 | 1.158
XHHW, XHHW-2, XHH | 700 kcmil | 640.2 | 0.9923 | 28.55 | 1.124
XHHW, XHHW-2, XHH | 600 kcmil | 561.9 | 0.8709 | 26.75 | 1.053
XHHW, XHHW-2, XHH | 500 kcmil | 450.6 | 0.6984 | 23.95 | 0.943
XHHW, XHHW-2, XHH | 400 kcmil | 373 | 0.5782 | 21.79 | 0.858
XHHW, XHHW-2, XHH | 350 kcmil | 333.3 | 0.5166 | 20.6 | 0.811
XHHW, XHHW-2, XHH | 300 kcmil | 292.6 | 0.4536 | 19.8 | 0.78
XHHW, XHHW-2, XHH | 250 kcmil | 251.9 | 0.3904 | 17.91 | 0.705
XHHW, XHHW-2, XHH | 4/0 AWG | 206.3 | 0.3197 | 16.21 | 0.638
XHHW, XHHW-2, XHH | 3/0 AWG | 170.5 | 0.2642 | 14.73 | 0.58
XHHW, XHHW-2, XHH | 2/0 AWG | 141.3 | 0.219 | 13.41 | 0.528
XHHW, XHHW-2, XHH | 1/0 AWG | 117.7 | 0.1825 | 12.24 | 0.482
XHHW, XHHW-2, XHH | 1 AWG | 98.97 | 0.1534 | 11.23 | 0.442
XHHW, ZW, XHHW-2, XHH | 2 AWG | 73.94 | 0.1146 | 9.703 | 0.382
XHHW, ZW, XHHW-2, XHH | 3 AWG | 62.06 | 0.0962 | 8.89 | 0.35
XHHW, ZW, XHHW-2, XHH | 4 AWG | 52.52 | 0.0814 | 8.179 | 0.322
XHHW, ZW, XHHW-2, XHH | 6 AWG | 38.06 | 0.059 | 6.96 | 0.274
XHHW, ZW, XHHW-2, XHH | 8 AWG | 28.19 | 0.0437 | 5.994 | 0.236
XHHW, ZW, XHHW-2, XHH | 10 AWG | 15.68 | 0.0243 | 4.47 | 0.176
XHHW, ZW, XHHW-2, XHH | 12 AWG | 11.68 | 0.0181 | 3.861 | 0.152
XHHW, ZW, XHHW-2, XHH | 14 AWG | 8.968 | 0.0139 | 3.378 | 0.133
Z | 1 AWG | 81.87 | 0.1269 | 10.21 | 0.402
Z | 2 AWG | 66.39 | 0.1029 | 9.159 | 0.36
Z | 3 AWG | 55.96 | 0.0865 | 8.382 | 0.33
Z | 4 AWG | 40.32 | 0.0625 | 7.163 | 0.282
Z | 6 AWG | 27.74 | 0.043 | 5.914 | 0.232
Z | 8 AWG | 19.78 | 0.0302 | 4.978 | 0.196
Z | 10 AWG | 12.32 | 0.0191 | 3.962 | 0.156
Z | 12 AWG | 7.548 | 0.0117 | 3.009 | 0.118
Z, ZF, ZFF, ZHF | 14 AWG | 5.355 | 0.0083 | 2.616 | 0.103
ZF, ZFF, ZHF | 16 AWG | 3.935 | 0.0061 | 2.235 | 0.088
ZF, ZFF, ZHF | 18 AWG | 2.903 | 0.0045 | 1.93 | 0.076

## EPICOR ELECTRIC PARTS
SEARCH WORD | EPICOR P/N | NEW P/N | EPICOR DESCRIPTION | NEW DESCRIPTION | SIZE | BIN LOCATION EC RACK | QTY | QTY BIN LOCATION 2 | NOTES
FASTENER |  | 241000208 |  | HEX HEAD SCREW M8 X 1.25 X 20 MM (PACKS OF 10 EACH) | M8 | EC6-3 |  |  | McMaster P/N 93635A318
TERMFITT |  | 241000135 |  | #1 AWG X 3/8" SINGLE COMP LUG | 1 AWG | EC5-4
WIRE |  | 241000162 |  | #1/0 AWG STRANDED WIRE THHN GREEN | #1/0 AWG | JOB
TERMFITT |  | 241000328 |  | #1/0 AWG X 1/2" SINGLE COMP LUGS | #1/0 AWG | EC5-4
TERMFITT |  | 241000164 |  | #1/0 AWG X 3/8" SINGLE COMPRESSION LUG | 1/0 AWG | EC5-4
FASTENER | 51000105 |  | HI-COLLAR L/W | #10 HI-COLLAR LOCKWASHER | #10 | MOVE TO CAGE AREA
WIRE | 90459365 |  |  | #14 AWG STRANDED WIRE GREEN | 14 AWG | EC-CABINET
WIRE | 50110061 |  |  | #14 AWG TFFN RED STRANDED WIRE | #14 AWG | CABINET
WIRE | 50110153 |  |  | #14 AWG THHN BLACK STRANDED WIRE | #14 AWG | CABINET
WIRE | 50110062 |  |  | #14 AWG THHN WHITE STRANDED WIRE | #14 AWG | CABINET
WIRE | 50110261 |  |  | #16 AWG AWG AWG TFFN BLACK STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110266 |  |  | #16 AWG AWG TFFN BLUE STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110299 |  |  | #16 AWG AWG TFFN GREEN / YELLOW STRIPE STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110264 |  |  | #16 AWG AWG TFFN GREEN STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110265 |  |  | #16 AWG AWG TFFN GREY STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110262 |  |  | #16 AWG AWG TFFN RED STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110300 |  |  | #16 AWG AWG TFFN WHITE / BLUE STRIPE STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110263 |  |  | #16 AWG AWG TFFN WHITE STRANDED WIRE | #16 AWG | CABINET
WIRE | 50110277 |  |  | #16 AWG AWG TFFN YELLOW STRANDED WIRE | #16 AWG | CABINET
TERMFITT |  | 241000137 |  | #2 AWG X 1/2" SINGLE COMP LUG | 2 AWG | EC5-4
TERMFITT |  | 241000136 |  | #2 AWG X 3/8" SINGLE COMP LUG | 2 AWG | EC5-4 | 20
WIRE |  | 241000156 |  | #2 AWG STRANDED WIRE THHN GREEN | #2 AWG | JOB
WIRE |  | 241000176 |  | #2 AWG X 3/8" SINGLE COMPRESSION LUG | #2 | JOB
WIRE | 90459367 |  |  | #2/0 AWG THHN BLACK STRANDED WIRE | #2/0 AWG | JOB
TERMFITT |  | 241000138 |  | #2/0 AWG X 3/8" SINGLE COMP LUG | 2/0 AWG | EC5-4
TERMFITT |  | 241000351 |  | #2/0 X 1/2" SINGLE COMPRESION LUG | #2/0 |  |  |  | McMaSTER P/N 6896K17
TERMFITT |  | 241000140 |  | #250 MCM X 3/8" SINGLE COMP LUG | 250 MCM | EC5-4
TERMFITT |  | 241000266 |  | #3 AWG X 3/8" SINGLE COMP LUG | #400 MCM | EC2-2
WIRE |  | 241000274 |  | #3/0 AWG GREEN STRANDED WIRE | #3/0 AWG | JOB
WIRE |  | 241000274 |  | #3/0 AWG STRANDED WIRE GREEN | #3/0 AWG | JOB
TERMFITT |  | 230000493 |  | #3/0 AWG X 1/2" SINGLE COMP LUG | 3/0 AWG | EC5-5 |  |  | MCMASTER P/N 6926K82
TERMFITT |  | 241000139 |  | #3/0 AWG X 3/8" SINGLE COMP LUG | 3/0 AWG | EC5-4 |  |  | MCMASTER P/N 6926K57
WIRE | 90459379 |  |  | #3/0 THHN BLACK STRANDED WIRE | #3/0 AWG | JOB
WIRE |  | 241000170 |  | #300 MCM CABLE | #300 MCM | JOB
TERMFITT |  | 241000272 |  | #300 MCM X 1/2" SINGLE COMPRESSION LUG | 1/2" | EC5-4
TERMFITT |  | 241000178 |  | #300 MCM X 3/8" SINGLE COMPRESSION LUG | #300 MCM | JOB
TERMFITT |  | 241000275 |  | #300 MCM X 5/8" SINGLE COMPRESSION LUG | 5/8" | EC5-4
TERMFITT |  | 241000278 |  | #350 MCM COMP LUG 5/8" STUD | 5/8" | EC5-4
WIRE |  | 241000152 |  | #350 MCM STRANDED WIRE THHN BLACK | #350 MCM | JOB
WIRE | 66600336 |  |  | #350 MCM THHN BLACK STRANDED WIRE | #350 MCM | JOB |  |  | INACTIVE DUPLICATE OF 241000152
TERMFITT |  | 241000009 |  | #350 MCM X 1/2" SINGLE COMP LUG | #350 MCM | EC5-4
TERMFITT |  | 241000268 |  | #350 MCM X 1/2" SINGLE COMPRESSION LUG | 1/2" | EC5-4
TERMFITT |  | 241000008 |  | #350 MCM X 3/8" SINGLE COMP LUG | #350 MCM | EC5-4 | 18
WIRE | 50110214 |  |  | #4 AWG THHN BLACK STRANDED WIRE | #4 AWG | JOB
TERMFITT |  | 241000148 |  | #4 X 1/4" SINGLE COMP LUG | 4 AWG | EC5-4
WIRE |  | 241000255 |  | #4/0 AWG THHN BLACK STRANDED WIRE | #4/0 AWG | ORDERED PER JOB
TERMFITT |  | 241000331 |  | #4/0 AWG X 1/4" SINGLE COMP LUGS | 1/4"
TERMFITT |  | 241000256 |  | #4/0 AWG X 3/8" SINGLE COMP LUG | #4/0 AWG | EC5-4
TERMFITT |  | 241000330 |  | #4/0 AWG X 5/16" SINGLE COMP LUGS | 5/16"
WIRE |  | 241000160 |  | #400 MCM STRANDED WIRE THHN | #400 MCM | JOB
TERMFITT |  | 241000349 |  | #400 MCM X 1/2" SINGLE COMPRESSION LUG
TERMFITT |  | 241000161 |  | #400 MCM X 3/8" SINGLE COMPRESSION LUG | 400 MCM | EC5-4
TERMFITT |  | 241000265 |  | #400 MCM X 5/8" SINGLE COMP LUG | #400 MCM | EC2-2
TERMFITT |  | 241000305 |  | #400 MCM X 5/8" SINGLE COMPRESSION LUG | #400 MCM | EC5-4
TERMFITT |  | 241000147 |  | #500 MCM X 3/8" SINGLE COMP LUG | 500 MCM | EC5-4
WIRE | 50110215 |  |  | #6 AWG THHN BLACK STRANDED WIRE | #6 AWG | JOB
WIRE | 50110271 |  |  | #6 AWG THHN GREEN STRANDED WIRE | #6 AWG | JOB
TERMFITT |  | 241000134 |  | #6 AWG X 1/4" SINGLE COMP LUG | 6 AWG | EC5-4
WIRE | 90459369 |  |  | #8 AWG THHN BLACK STRANDED WIRE | #8 AWG | JOB
WIRE |  | 241000302 |  | #8 AWG THHN RED STRANDED WIRE | #8 AWG | WIRE RACK
WIRE |  | 241000303 |  | #8 AWG THHN WHITE STRANDED WIRE | #8 AWG | WIRE RACK
FASTENER | 51000107 |  | SPLIT LOCKWASHER GR 8 YELLOW ZN | #8 SPLIT RING LOCKWASHER ZINC YELLOW | #8 | MOVE TO CAGE AREA
HEATSHNK | 53460144 |  | GREEN/YELLOW HEAT SHRINK TUBING | 0.12 GREEN / YELLOW HEAT SHRINK TUBING | 0.125" | CABINET
HEATSHNK | 53460141 |  | WHITE HEAT SHRINK TUBING | 0.19 WHITE HEAT SHRINK TUBING | .19" | CABINET
CONDFITT | 40000055 |  |  | 1 1/2" LIQ-TIGHT 90 DEG CONN | 1-1/2" | JOB
CONDBODY | 50113048 |  | CROUSE-HINDS VER./HOR. M/F SEAL CONDFITT | 1" MALL SEAL OFF COND FITT EYS | 1" | EC1-3 | 13
CONDBODY | 50111403 |  | CROUSE-HINDS MALL T CONDBODY | 1" MALL T COND BODY | 1" | EC1-3
KOSEAL |  | 241000063 |  | 1" 3 PIECE K.O. SEAL TYPE 1 | 1" | EC4-4 | 62
CONDFITT |  | 241000125 |  | 1" 90 DEG. PULL ELB FEM / FEM NON HAZ LOC | 1" | EC1-3 | 11
CONDBODY | 50113202 |  |  | 1" COND BODY COVER / FM7 | 1" | EC1-3 | 42 |  | ADDED TO MASTER LIST
CONDBODY |  | 241000209 |  | 1" COND BODY GASKET / FM7 | 1" | EC3-1 | 46 |  | NEW PART NUMBER / LABEL
CONDBODY | 50113004 |  | 1" neoprene cover gasket (Topaz 583) | 1" CONDUIT BODY GASKET SCREW TYPE | 1" | EC1-3 | 29 | 45
CORDGRIP | 49360025 |  | SEALCON 1" NPT 4 HOLE .37" CORDGRIP | 1" CORDGRIP X 4 HOLES 0.37" | 1" | EC4-3
CONDFITT |  | 241000316 |  | 1" ERICKSON FEMALE / FEMALE UNION NON HAZARDOUS | 1/2" | EC2-4
NIPPLE | 50110082 |  | 1" X CLOSE COND NIPPLE | 1" GRC CLOSE NIPPLE | 1" | EC1-3 | 41
CONDUIT | 50110108 |  | RIGID GALVANIZED COND | 1" GRC CONDUIT | 1" | B5- COND RACK
CONDFITT |  | 241000123 |  | 1" GRC STRUT STRAPS | 1" | EC1-3
CONDBODY |  | 241000087 |  | 1" GRL ALUM COND BODY | 1" | EC1-3 | 3
CONDFITT | 30304203 |  | HOFFMAN HOLE PLUG | 1" HOFFMAN HOLE PLUG 3 PIECE TYPE 4 | 1" | EC4-4 | 73
CONDFITT | 50113252 |  | CROUSE-HINDS METALIC SEALTIGHT 45 DEG. | 1" LIQ-TIGHT 45 DEG CONN | 1" | EC2-3 | 20 |  | DESC CHANGE
CONDUIT | 50113268 |  |  | 1" LIQ-TIGHT FLEX | 1" | JOB
CONDFITT | 50113256 |  | CROUSE-HINDS METALIC SEALTIGHT 90 DEG. | 1" LIQ-TIGHT LIQ TIGHT 90 DEG CONN | 1" | EC2-3 | 50 |  | DESC CHANGE
CONDFITT | 50113264 |  | LIQTIGHT SEAL RING ASSY. T & B | 1" LIQ-TIGHT SEAL RING | 1" | EC4-4 | 146
CONDFITT | 50113260 |  | CROUSE-HINDS METALIC STRAIGHT CONN. | 1" LIQ-TIGHT STRAIGHT CONN | 1" | EC2-3 | 45 |  | DESC CHANGE
CONDFITT | 50110119 |  | LOCK RING | 1" LOCK RING | 1" | EC4-4 | 580
CONDBODY |  | 241000121 |  | 1" MALL C COND BODY | 1" | EC1-3 | 9 | 8
CONDBODY | 50113201 |  | 1" MALL CONDBODY COVER CROUSE-HINDS K100M | 1" MALL COND BODY COVER / SCREW TYPE | 1" | EC1-3 | 11 | 35 | TWO DIFFERENT BINS
CONDBODY |  | 241000118 |  | 1" MALL LB COND BODY | 1" | EC1-3 | 2 | 22
CONDBODY |  | 241000090 |  | 1" MALL LBY COND BODY | 1" | EC1-3 | 4
CONDBODY |  | 241000119 |  | 1" MALL LL CONDUIT BODY | 1" | EC1-3 | 1 | 7
CONDBODY |  | 241000120 |  | 1" MALL LR COND BODY / FM7 | 1" | EC1-3 | 3 | 13 | TWO DIFFERENT BINS
CONDBODY |  | 241000185 |  | 1" MALL T COND BODY | 1" | EC1-3 | 3 | 11
CONDBODY |  | 241000122 |  | 1" MALL TB CONDUIT BODY | 1" | EC1-3 |  | 9
CONDBODY | 50111406 |  | CRHI X100M 1" MALL "X" CONDBODY | 1" MALL X COND BODY | 1" | EC1-3
CONDBODY |  | 241000199 |  | 1" MALL X CONDUIT BODY | 1" | EC1-1
CONDFITT | 50110023 |  |  | 1" MEYERS HUB | 1" | EC2-3 | 41 |  | INACTIVE
CONDFITT | 50110859 |  | CROUSE-HINDS MEYERS HUB (GROUND) | 1" MEYERS HUB | 1" | EC2-3 |  |  | DUPLICATE
CONDFITT |  | 241000108 |  | 1" PULL ELB MALE / FEM TYPE 1 | 1" | EC2-3
CONDSUPP | 50110151 |  | 1" COND CLAMPS CROUS-HINDS RAC100HD | 1" RA COND CLAMPS | 1" | EC1-3 | 80
CONDFITT |  | 241000012 |  | 1" REC HOLE PLUG | 1" | EC2-2 | 40
CONDFITT |  | 241000091 |  | 1" SHORT COND ELB HAZ LOC | 1" | EC2-3 | 81
CONDFITT |  | 241000124 |  | 1" SHORT COND ELB MALE / FEM NON HAZ LOC | 1" | EC3-2
CONDFITT |  | 241000284 |  | 1" STRUT STRAPS / EMT | 1" | EC-3
CONDFITT | 50110073 |  |  | 1" THREADED COUPLING | 1" | EC1-3 | 18 |  | ADDED TO MASTER LIST
BUSHING | 50110123 |  | RE BUSHING 1" x 1/2" TOPAZ RB3 | 1" x 1/2" RE BUSHING | 1" | EC1-4 | 18
CONDFITT |  | 241000059 |  | 1" X 1/2" RED WASHERS | 1" | EC5-4
TERMFITT |  | 241000149 |  | 1" X 1/2" REDUCING WASHERS | 1" X 1/2" | EC5-4
NIPPLE |  | 241000107 |  | 1" x 2" GRC NIPPLE | 1" | EC1-3 | 0
NIPPLE | 50110320 |  |  | 1" X 3" GRC COND NIPPLE | 1" X 3" | EC1-3
BUSHING | 50110125 |  | CROUSE-HINDS RE BUSHING | 1" X 3/4" RE BUSHING | 1" | EC4-3 | 77
REWASH | 50110072 |  |  | 1" X 3/4" RE WASHER | 1" X 3/4" | EC3-2
NIPPLE | 50110321 |  | 1" X 4" COND NIPPLE | 1" X 4" GRC NIPPLE | 1" | EC1-3 | 0
NIPPLE | 50110322 |  |  | 1" X 5" GRC COND NIPPLE | 1" X 5" | OBSOLETE
NIPPLE | 50110323 |  |  | 1" X 6" GRC COND NIPPLE | 1" X 6" | OBSOLETE
CONDFITT | 50111048 |  | CROUSE-HINDS VER./HOR. M/F SEAL CONDFITT | 1/2" MALL SEAL OFF CONDUIT FITTING EYS | 1/2" | EC3-2 | 35
KOSEAL |  | 241000017 |  | 1/2" 3 PIECE K.O. SEAL TYPE 1 | 1/2" | EC4-4 | 170
CORDGRIP | 50110855 |  | CROUSE-HINDS, 1/2" NPT, 45 deg, 0.45", STRAIN RELIEF CORD GRIP | 1/2" 45 DEG CORDGRIP X 1 HOLE 0.45" | 1/2" | EC5-4 | 56
CORDGRIP | 49360027 |  | CROUSE-HINDS, 1/2" NPT, 90 deg, 0.25"-0.35", STRAIN RELIEF CORD GRIP | 1/2" 90 DEG CORDGRIP X 1 HOLE 0.25"-0.35" | 1/2" | EC5-4
CORDGRIP | 49360026 |  | CROUSE-HINDS, 1/2" NPT, 90 deg, 0.35"-0.45", STRAIN RELIEF CORD GRIP CG5090-450 | 1/2" 90 DEG CORDGRIP X 1 HOLE 0.35"-0.45" | 1/2" | EC5-4
CONDFITT | 50110011 |  | 1/2" 90 COND CORNER ELB FF050 | 1/2" 90 DEG ELB / FEM / FEM HAZ LOC | 1/2" | EC3-3 | 9 |  | NEW DESCRIPTION
CONDFITT | 50110005 |  | CROUSE-HINDS 90 DEG. PULL ELB M/F | 1/2" 90 DEG. PULL ELB FEM / FEM NON HAZ LOC | 1/2" | EC3-2 | 73
CONDFITT | 50110005 |  |  | 1/2" 90 DEGREE PULLING ELBOW | 1/2" | EC3-2 | 73
LABELS | 49358982 |  | BRADY BMP-21+ PRINTER LABELS | 1/2" BRADY BMP-21+ PRINTER LABELS | MISC | CABINET | 21
CONDFITT | 50110077 |  |  | 1/2" CHASE NIPPLE | 1/2" | OBSOLETE
CONDBODY | 35000032 |  | 1/2" CONDBODY COVER GASKET CROUSE HINDS GK50N | 1/2" CONDBODY COVER GASKET | 1/2" | EC3-4 | 42
TERMFITT | 50140042 |  |  | 1/2" CONDUIT ADAPATOR FOR 4-WAY CONTROL VALVE | 1/2" | MOVE TO 400 CAGE AREA
CONDBODY |  | 241000234 |  | 1/2" CONDUIT BODY COVER SCREW TYPE | 1/2" | EC3-4
CONDBODY |  | 241000233 |  | 1/2" CONDUIT BODY COVER GASKET SCREW TYPE | 1/2" | EC3-4
CONDFITT |  | 241000050 |  | 1/2" CORD GRIP .28" NON / STANDARD | 1/2" | EC5-4 | 68
CORDGRIP | 49360021 |  | SEALCON 1/2" NPT 1 HOLE .28" CORDGRIP | 1/2" CORDGRIP X 1 HOLE 0.28" | 1/2" | EC4-3 | 40
CONDFITT | 50111248 |  | DRAIN BREATHER | 1/2" DRAIN BREATHER | 1/2" | EC3-2 | 25 |  | DESCRIPTION CHANGE
CONDFITT |  | 241000097 |  | 1/2" ELF 45 DEG ELB HAZ LOC | 1/2" | EC3-3 | 9
CONDFITT |  | 241000315 |  | 1/2" ERICKSON FEMALE / FEMALE UNION NON HAZARDOUS | 1/2" | EC2-3
FASTENER |  | 241000102 |  | 1/2" FLAT WASHERS SS | 1/2" | EC5-3 | 0 |  | P/N #92141A033
NIPPLE | 50110052 |  | RIGID CONDCOND CLOSE NIPPLE | 1/2" GRC CLOSE NIPPLE | 1/2" | EC3-3 | 67
CONDUIT | 50110012 |  | RIGID GALVANIZED COND | 1/2" GRC CONDUIT | 1/2" | B5- COND RACK
CONDFITT |  | 241000115 |  | 1/2" GRC STRUT STRAPS | 1/2" | EC2-2
CONDBODY |  | 241000043 |  | 1/2" GRL AL COND BODY HAZ LOC | 1/2" | EC3-4 | 10
FASTENER |  | 241000269 |  | 1/2" HEX NUT STAINLESS STEEL | 1/2" | EC5-3 |  |  | P/N #6926K46
CONDFITT | 30304201 | ` | HOFFMAN HOLE PLUG | 1/2" HOFFMAN HOLE PLUG 3 PIECE TYPE 4 | 1/2" | EC4-4 | 34
KOSEAL |  | 241000166 |  | 1/2" KO SEAL FOR MYPRO PANEL 7/8" HOLE SIZE / GREY P/N 1EMR2 | 1/2" | EC4-4
CONDBODY |  | 241000224 |  | 1/2" LB ALUMINUM CONDUIT BIDIES | 1/2" | EC3-4 | 21 |  | NEW PART NUMBER / LABEL
CONDBODY |  | 241000165 |  | 1/2" LB COVER AND GASKET / CAST ALUMINUM | 1/2" | EC3-4
CONDFITT |  | 241000214 |  | 1/2" LIQ TIGHT 45 DEG ELBOW / | 1/2" | EC3-2 | 84 |  | NEW PART NUMBER / LABEL TWO BIN LOCATIONS
CONDFITT |  | 241000215 |  | 1/2" LIQ TIGHT 90 DEG ELBOW / | 1/2" | EC3-2 | 145 |  | NEW PART NUMBER / LABEL TWO BIN LOCATIONS
CONDFITT |  | 241000213 |  | 1/2" LIQ TIGHT STRAIGHT CONN / | 1/2" | EC3-2 | 202 |  | NEW PART NUMBER / LABEL TWO BIN LOCATIONS
CONDFITT | 50110859 |  | CROUSE-HINDS METALIC SEALTIGHT 45 DEG. | 1/2" LIQ-TIGHT 45 DEG CONN / WITH GROUND | 1/2" | EC3-1 | 59 |  | DESCRIPTION CHANGE
CONDFITT | 50111256 |  | CROUSE-HINDS METALIC SEALTIGHT 90 DEG. | 1/2" LIQ-TIGHT 90 DEG CONN / WITH GROUND | 1/2" | EC3-1 | 109 |  | DESCRPTION CHANGE / IN TWO BINS
CONDUIT | 50111268 |  | 1/2" FLEX COND METALLIC **MUST BE UL LISTED** | 1/2" LIQ-TIGHT FLEX COND | 1/2" | GREENLEE BOX
CONDFITT | 50111264 |  | LIQTIGHT SEAL RING ASSY. T & B | 1/2" LIQ-TIGHT SEAL RING | 1/2" | EC3-4 | 763
CONDFITT | 50111260 |  |  | 1/2" LIQ-TIGHT STRAIGHT CONN / WITH GROUND | 1/2" | EC3-2 | 126 |  | DESCRPTION CHANGE / IN TWO BINS
CONDFITT | 50110028 |  | LOCK RING | 1/2" LOCK RING | 1/2" | EC4-4 | 35
CONDFITT | 50110005 |  |  | 1/2" MALE / FEM PULLING ELB | 1/2" | EC3-2
CONDBODY | 50111405 |  |  | 1/2" MALL C CONDUIT BODY | 1/2" | EC3-4 | 3 | 36 | 2 SEPARATE BIN LOCATIONS
CONDBODY | 50111205 |  |  | 1/2" MALL COND BODY COVER / FM7 | 1/2" | EC3-4 | 27 | 38 | DESCRIPTION CHANGE
CONDBODY | 50111004 |  |  | 1/2" MALL COND BODY GASKET / FM7 | 1/2" | EC3-4 | 42 |  | DESCRIPTION CHANGE
CONDBODY | 50111204 |  | CROUSE-HINDS MALL LB CONDBODY | 1/2" MALL LB COND BODY | 1/2" | EC3-4 | 14
CONDBODY |  | 241000095 |  | 1/2" MALL LBY FEM / FEM COND BODY | 1/2" | EC3-3 | 5
CONDBODY |  | 241000111 |  | 1/2" MALL LL CONDUIT BODY | 1/2" | EC3-4 |  | 12 | On the label
CONDBODY | 50111220 |  |  | 1/2" MALL LR COND BODY | 1/2" | EC3-4 | 6 | 19
CONDBODY | 50111203 |  | CROUSE-HINDS MALL T CONDBODY | 1/2" MALL T COND BODY | 1/2" | EC3-4 | 1 | 19
CONDBODY |  | 241000113 |  | 1/2" MALL TB CONDUIT BODY | 1/2" | EC3-3 |  | 25 | 2 SEPARATE BIN LOCATIONS
CONDFITT |  | 241000110 |  | 1/2" MALL UNION 90 HAZ LOC UNL | 1/2" | EC3-3 | 28
CONDFITT | 50111240 |  | 1/2" MALL UNION MALE/FEM CROUS-HINDS UNY-105 | 1/2" MALL UNION MALE / FEM UNY HAZ LOCATION | 1/2" | EC3-2 | 71
CONDBODY |  | 241000114 |  | 1/2" MALL X CONDUIT BODY | 1/2" | EC1-2 | 8 | 25
CONDFITT | 50110861 |  | MEYERS HUB (GROUND) | 1/2" MEYERS HUB | 1/2" | EC3-3 | 79 | 20
CORDGRIP |  | 241000335 |  | 1/2" NPT BLACK NYLON CORD GRIP (.39-.55) | 1/2"
CONDBODY | 49360058 |  | CROUSE-HINDS 1/2" NPT MALE/FEM SHORT COND ELB CLASS 1 DIV 11 (EL196) | 1/2" NPT MALE / FEM SHORT COND ELB | 1/2" | EC3-2 | 48
KOSEAL |  | 241000053 |  | 1/2" NPT PLASTIC HOLE PLUG | 1/2" | EC5-4 | 248
CONDFITT | 53460151 |  | HOLE PLUG LOCKING PANEL PLUGS | 1/2" NYLON PLASTIC HOLE PLUG | 1/2" | EC4-4 | 4464
CONDSUPP | 50110014 |  | 1/2" COND CLAMPS CROUS- HINDS RAC50HD | 1/2" RA COND CLAMPS | 1/2" | EC3-3 | 217
CONDFITT |  | 241000010 |  | 1/2" REC HOLE PLUG | 1/2" | EC3-3 | 13
CONDFITT | 50111244 |  | T & B SHORT COND ELB | 1/2" SHORT COND ELB MALE / FEM NON HAZ LOC | 1/2" | EC3-2 | 74
FASTENER |  | 241000060 |  | 1/2" SPLIT WASHERS SS | 1" | EC5-3 | 46 |  | PART NUMBER CHANGE
FASTENER |  | 241000103 |  | 1/2" SPLIT WASHERS SS | 1/2" | EC5-3 |  |  | P/N #92146A033
CONDFITT |  | 241000282 |  | 1/2" STRUT STRAPS / EMT | 1/2" | EC-3
CONDFITT | 50110013 |  |  | 1/2" THREADED GRC COUPLING | 1/2" | EC3-4
CONDFITT | 50111240 |  |  | 1/2" UNION MALE / FEM HAZ LOC | 1/2" | EC3-2
NIPPLE |  | 241000096 |  | 1/2" X 2" GRC NIPPLE | 1/2" | EC3-3 | 77
FASTENER |  | 241000273 |  | 1/2" X 20" X 1-1/2" HEX CAP SCREW | 1/2" | EC5-3 |  |  | P/N #92241A435
NIPPLE | 50110056 |  | ELEC GALV NIPPLE .5" X 3" | 1/2" X 3" GRC NIPPLE | 1/2" | EC3-3 | 22
NIPPLE | 50110057 |  |  | 1/2" x 4" GRC Nipple | 1/2" | EC3-3 | 15
NIPPLE | 50110107 |  |  | 1/2" X 5" NIPPLE | 1/2" | OBSOLETE
NIPPLE | 50110058 |  |  | 1/2" X 6" NIPPLE | 1/2" | OBSOLETE
FASTENER |  | 241000024 |  | 1/4" FLAT WASHER SS PACK OF 100 EACH | 1/4" | EC5-3 | 458 |  | MCMASTER P/N 92141A029
NIPPLE | 50164404 |  | NIPPLE | 1/4" NPT CARBON STEEL CLOSE NIPPLE | 1/4" | MOVE TO CAGE AREA
NIPPLE | 50160534 |  | COUPLING | 1/4" NPT CARBON STEEL COUPLING | 1/4" | MOVE TO CAGE AREA
FASTENER |  | 241000025 |  | 1/4" NYLON INSERT HEX LOCKNUT SS PACK OF 100 EACH | 1/4" | EC5-3 | 168 |  | MCMASTER P/N 90715A125
CONDFITT |  | 241000196 |  | 1/4" REC PLUG | 1-1/4" X 3/4" | EC1-4
SPLITUBE |  | 241000341 |  | 1/4" SPLIT TUBING BLACK | 1/4" |  |  |  | MCMASTER P/N 7840K71
SPLITUBE |  | 241000190 |  | 1/4" SPLIT TUBING BLACK 100'/ ROLL | 1/4" | EC-CAB |  |  | MCMASTER P/N 7840K71
FASTENER | 51000106 |  | HI-COLLAR L/W ZINC PLATED | 1/4" SPLIT WASHER PACK OF 100 EACH | 1/4" | MOVE TO CAGE AREA |  |  | MCMASTER P/N 92146A029
FASTENER |  | 241000054 |  | 1/4" SPLIT WASHERS SS | 1/4"-20 | EC5-3 | 467
FASTENER |  | 241000052 |  | 1/4"-20 HEX NUTS SS | 1/4"-20 | EC5-3 | 513
FASTENER |  | 241000023 |  | 1/4"-20 X 1/2" HEX HEAD CAP SCREW SS PACK OF 50 EACH | 1/4"- 20 | EC5-3 | 75 |  | MCMASTER P/N 92240A537
FASTENER |  | 241000051 |  | 1/4"-20 X 1/4" PHILLIPS SCREW SS | 1/4"-20 | EC5-3 | 49
FASTENER | 100011406 |  | 1/4" X 20 X 1 3/4" HEX SOCKET SCREW | 1/4"-20 X 1-3/4" HEX SOCKET SCREW | 1/4" | MOVE TO CAGE AREA
FASTENER |  | 241000022 |  | 1/4"-20 X 3/4" HEX HEAD CAP SCREW SS PACK OF 50 EACH | 1/4"- 20 | EC5-3 | 505 |  | MCMASTER P/N 92240A537
NEXT AVAILABLE |  | 241000366 |  | 1/6" VIOLET HEAT SHRINK |  | EC-CABINET
HEATSHNK |  | 241000342 |  | 1/8" RED HEAT SHRINK | 1/8"
CONDFITT | 50113240 |  | CROUSE-HINDS UNY-305 1” MALE/FEM UNION | 1” MALE / FEM UNION UNY | 1" | EC2-3 | 36
ENCLOSURE |  | 241000312 |  | 10" X 10" MOUNTING PANEL | 8.75 X 8.88 | ELECTRICAL CABINET |  |  | HOFF A10P10
ENCLOSUR |  | 241000311 |  | 10" x 10" x 6" CONT HINGE TYPE 4 WITH CLAMPS | 10" X 10" X 6" | ELECTRICAL CABINET |  |  | HOFF 10106 CHNF
FASTENER | 51000578 |  |  | 10-24 X 1-1/4" SOCKET HEAD SCREW | 10-24 X 1-1/4 | DO NOT USE
HARDWARE | 51000579 |  |  | 10-24 X 2-3/4" LONG SOCKET HEAD CAP SCREW, ALLOY STEEL
TERMFITT | 66600371 |  |  | 10-32 GREEN GROUND SCREW | 10-32 | EC5-3
FASTENER |  | 241000020 |  | 10-32 X 1/2" PHILLIPS SCREW | 10-32 | EC5-3 | 198
FASTENER |  | 241000021 |  | 10-32 X 1/4" PHILLIPS SCREW | 10-32 | EC5-3 | 442
NIPPLE |  | 241000250 |  | 1-1/2" CHASE NIPPLE | 1-1/2" | EC2-1
CONDUIT | 50110249 |  |  | 1-1/2" GRC CONDUIT | 1-1/2" | JOB
CONDFITT | 50110227 |  | CROUSE-HINDS METALIC SEALTIGHT 45 DEG. | 1-1/2" LIQ-TIGHT 45 DEG CONN | 1-1/2" | EC2-1
CONDFITT | 40000055 |  | CROUSE-HINDS METALIC SEALTIGHT 90 DEG. | 1-1/2" LIQ-TIGHT 90 DEG CONN / WITH GROUND | 1-1/2" | EC2-1 | 5 |  | DESCRIPTION CHANGE
CONDUIT | 50110225 |  |  | 1-1/2" LIQ-TIGHT FLEX | 1-1/2" | JOB
CONDFITT | 50110276 |  | COND SEALING RING | 1-1/2" LIQ-TIGHT SEALING RING | 1-1/2" | EC4-2
CONDFITT | 50110226 |  | CROUSE-HINDS METALIC STRAIGHT CONN. | 1-1/2" LIQ-TIGHT STRAIGHT CONN | 1-1/2" | EC2-1 | 5
CONDFITT |  | 241000252 |  | 1-1/2" LOCKNUT | 1-1/2" | EC2-1
CONDFITT | 50110228 |  |  | 1-1/2" MALL RA CLAMP | 1-1/2" | JOB
CONDBODY | 50111049 |  | 1 1/2" MALL VERTICAL/HORIZONTAL SEAL CONDFITT FEM/FEM | 1-1/2" MALL SEAL OFF COND FITT EYS | 1-1/2" | EC2-1 | 4 |  | DESCRIPTION CHANGE
CONDBODY | 50111402 |  | CRHI T150M 1-1/2" MALL CONDBODY | 1-1/2" MALL T COND BODY | 1-1/2" | EC1-1 |  | 1
CONDFITT |  | 241000086 |  | 1-1/2" MEYERS HUB | 1-1/2" | EC2-1 | 28
CONDFITT | 50110856 |  | CROUSE-HINDS MEYERS HUB (GROUND) | 1-1/2" MEYERS HUB | 1-1/2" | EC1-1 | 14
BUSHING |  | 241000254 |  | 1-1/2" PLASTIC BUSHING | 1-1/2" | EC2-1
CONDFITT |  | 241000015 |  | 1-1/2" REC HOLE PLUG | 1-1/2" | EC2-1 | 1
CONDFITT | 50110235 |  |  | 1-1/2" RIDGID THREADED COUPLING | 1-1/2" | JOB
CONDFITT |  | 241000285 |  | 1-1/2" STRUT STRAPS EMT | 1-1/2" | EC-3
BUSHING |  | 241000218 |  | 1-1/2" x 1" RE BUSHING | 1-1/2" X 1" | EC1-1 | 12 |  | NEW PART NUMBER / LABEL
CONDFITT | 50110236 |  |  | 1-1/2" x 1" RE BUSHING | 1-1/2" | JOB
BUSHING | 50110236 |  | CROUSE-HINDS RE BUSHING | 1-1/2" X 1-1/4" RE BUSHING | 1-1/2" | EC1-1 | 5 |  | DESCRIPTION CHANGE
BUSHING |  | 241000247 |  | 1-1/2" x 3/4" REDUCING BUSHING | 1-1/2" x 3/4" | EC7-5
NIPPLE |  | 241000106 |  | 1-1/2" X GRC CLOSE NIPPLE | 1-1/2" | EC1-1 | 6 |  | DESCRIPTION CHANGE / NEED LABEL
CONDFITT | 50110325 |  |  | 1-1/2"x 1 1/4" RE BUSHING | 1-1/2" | EC1-4 |  |  | ADD BIN LOCATION
CONDFITT | 50110324 |  |  | 1-1/2"x CLOSE NIPPLE | 1-1/2" | JOB | 6
CONDFITT | 50110216 |  | 1-1/4'' COND CLAMP (CROUS-HINDS RAC125HD) | 1-1/4'' RA COND CLAMPS | 1-1/4" | EC1-4 | 29
CONDFITT | 50110857 |  | CROUSE-HINDS VER./HOR. M/F SEAL CONDFITT | 1-1/4" MALL SEAL OFF COND FITT EYS / VERT - HORIZONTLE | 1-1/4" | EC1-4 | 15
BUSHING |  | 241000249 |  | 1-1/4" CHASE NIPPLE | 1-1/4" | EC2-4
CONDBODY | 50113304 |  |  | 1-1/4" COND BODY COVER GASKET / SCREW TYPE | 1-1/4" | EC1-4 | 10 |  | DESCRIPTION CHANGE
CONDFITT | 50113368 |  |  | 1-1/4" CONDUIT SEALING RING | 1-1/4" | EC6-4
CONDFITT |  | 241000310 |  | 1-1/4" ERICKSON FEMALE / FEMALE UNION NON HAZARDOUS | 1-1/4"
CONDFITT |  | 241000088 |  | 1-1/4" EYF MALL SEAL OFF / VERTICLE | 1-1/4" | EC1-4 | 1
NIPPLE | 50110293 |  | 1 1/4" x close COND nipple | 1-1/4" GRC CLOSE NIPPLE | 1-1/4" | EC1-4 | 14
CONDUIT | 50110109 |  | RIGID GALVANIZED COND | 1-1/4" GRC CONDUIT | 1-1/4" | B5- COND RACK
CONDFITT | 50110186 |  | 1 1/4" EMT STRUT STRAPS | 1-1/4" GRC STRUT STRAPS | 1-1/4" | EC1-4
CONDFITT |  | 241000211 |  | 1-1/4" LIQ TIGHT 45 DEG ELBOW / WITH GROUND | 1-1/4" | EC2-4 | 10 |  | NEW PART NUMBER / LABEL
CONDFITT |  | 241000212 |  | 1-1/4" LIQ TIGHT STRAIGHT CONNECTOR / WITH GROUND | 1-1/4" | EC2-4 | 6 |  | NEW PART NUMBER / LABEL
CONDFITT | 50113352 |  | CROUSE-HINDS METALIC SEALTIGHT 45 DEG. | 1-1/4" LIQ-TIGHT 45 DEG CONN | 1-1/4" | EC2-4 | 7 |  | DESC CHANGE
CONDFITT | 50113358 |  | CROUSE-HINDS METALIC SEALTIGHT 90 DEG. | 1-1/4" LIQ-TIGHT 90 DEG CONN | 1-1/4" | EC2-4 | 27 |  | DESC CHANGE
CONDUIT |  | 241000232 |  | 1-1/4" LIQ-TIGHT FLEX | 1-1/4" | B5-CONDUIT RACK
CONDFITT | 50111269 |  | METALIC SEALING RING UL LISTED SEALTIGHT | 1-1/4" LIQ-TIGHT SEALING RING | 1-1/4" | EC4-2
CONDFITT | 50113362 |  | CROUSE- HINDS METALIC STRAIGHT CONN. | 1-1/4" LIQ-TIGHT STRAIGHT CONN | 1-1/4" | EC2-4 | 13 |  | DESC CHANGE
CONDFITT |  | 241000132 |  | 1-1/4" LOCK RING | 1-1/4" | EC5-4
NIPPLE |  | 241000251 |  | 1-1/4" LOCKNUT | 1-1/4" | EC2-4
CONDBODY |  | 241000129 |  | 1-1/4" MALL C COND BODY | 1-1/4" | EC1-4 | 2
CONDBODY | 49360062 |  | CROUSE HINDS 1-1/4 & 1-1/2" MALL CONDBODY COVERS, SCREW TYPE | 1-1/4" MALL COND BODY COVER / FM7 | 1-1/4" | EC1-4 | 94 |  | DESCRIPTION CHANGE
CONDBODY |  | 241000183 |  | 1-1/4" MALL COND BODY COVER / SCREW TYPE | 1-1/4" | EC1-4 | 13 | 7 | NEW PART NUMBER / LABEL
CONDBODY |  | 241000184 |  | 1-1/4" MALL COND BODY GASKET / FM7 | 1-1/4" | EC1-4 | 89 | 34 | CHANGE DESCRIPTION
CONDBODY |  | 241000042 |  | 1-1/4" MALL FEM / FEM UNION | 1-1/4" | EC1-4 | 4
CONDBODY |  | 241000126 |  | 1-1/4" MALL LB COND BODY | 1-1/4" | EC1-3 |  | 7
CONDBODY |  | 241000089 |  | 1-1/4" MALL LBY HAZ LOC | 1-1/4" | EC1-4 | 2
CONDBODY |  | 241000133 |  | 1-1/4" MALL LBY HAZ LOC | 1-1/4" | EC1-4
CONDBODY |  | 241000040 |  | 1-1/4" MALL LL COND BODY | 1-1/4" | EC1-4 | 4
CONDBODY |  | 241000127 |  | 1-1/4" MALL LL CONDUIT BODY | 1-1/4" | EC1-4
CONDBODY |  | 241000041 |  | 1-1/4" MALL LR COND BODY | 1-1/4" | EC1-4 | 7
CONDBODY |  | 241000128 |  | 1-1/4" MALL LR COND BODY | 1-1/4" | EC1-4 | 7 | 2
CONDBODY |  | 241000179 |  | 1-1/4" MALL T COND BODY | 1-1/4" | EC1-4 | 11 | 4
CONDBODY | 50111401 |  | CROUSE-HINDSMALL T CONDBODY | 1-1/4" MALL T COND BODY | 1-1/4" | EC1-4 | 1
CONDBODY |  | 241000130 |  | 1-1/4" MALL TB CONDUIT BODY | 1-1/4" | EC1-4 | 2 | 12 | TWO BIN LOCATIONS
CONDFITT |  | 241000131 |  | 1-1/4" MALL UNION MALE / FEM UNY | 1-1/4" | EC2-4
CONDBODY | 50111400 |  | CROUSE-HINDS MALL X CONDBODY | 1-1/4" MALL X COND BODY | 1-1/4" | EC1-4 | 1 | 4
CONDFITT | 50110858 |  | CROUSE-HINDS, 1 1/4" HAZARDOUS LOCATION MEYERSS HUB (STGK4) | 1-1/4" MEYERS HUB | 1-1/4" | EC1-4 | 6
CONDFITT |  | 241000253 |  | 1-1/4" PLASTIC BUSHING | 1-1/4" | EC2-4
CONDFITT |  | 241000014 |  | 1-1/4" REC HOLE PLUG | 1-1/4" | EC1-3 | 3 |  | NEW BIN LOCATION
CONDFITT | 40000047 |  | 1-1/4" rigid COND coupling | 1-1/4" RIGID COND COUPLING | 1-1/4" | EC1-4
SPLITUBE |  | 241000321 |  | 1-1/4" SPLIT TUBING BLACK 100'/ ROLL | 1-1/4" | ELECTRICAL CABINET
CONDFITT |  | 241000210 |  | 1-1/4" THREADED GRC COUPLING | 1-1/4" | EC2-4 | 13 |  | NEW PART NUMBER / LABEL
BUSHING | 50110110 |  | RE BUSHING 1.25" x 1" | 1-1/4" x 1" RE BUSHING | 1-1/4" | EC1-4 | 52
BUSHING | 40000048 |  | 1 1/4" x 1/2" ELECTRICAL RE BUSHING | 1-1/4" x 1/2" RE BUSHING | 1-1/4" | EC1-4 | 23
BUSHING |  | 49360061 |  | 1-1/4" X 1/2" REDUCING BUSHING | 1-1/4" X 1/2" | EC2-4 | 23
NIPPLE |  | 241000105 |  | 1-1/4" X 2" GRC NIPPLE | 1-1/4" | EC1-4
BUSHING |  | 241000201 |  | 1-1/4" X 3/4" RE BUSHING | 1-1/4" X 3/4" | EC2-4 | 48 |  | BIN LOCATION NEEDS LABEL
CABLE |  | 241000332 |  | 12-4 600 VOLT UN-SHLD CABLE | 12-4 COND
CABLE | 40000056 |  | OMI CABLE A11403 14/3 TCER | 14/3 TCER 600V / DIGITAL HEATER CABLE | 14 AWG | B5- COND RACK
LABELS |  | 241000193 |  | 1-5/8 X 1-5/8 Multi Hole | 1-5/8 X 1-5/8 | BK5-COND RK
STRUT | 50110796 |  |  | 1-5/8" STRUT BLACK PLASTIC COVER | 1-5/8" | EC4-4 |  |  | (Mcmaster carr 3204T96)
STRUT | 50110201 |  | BLACK STRUT END CAP 1 5/8" X 1 5/8" | 1-5/8" x 1-5/8" BLACK STRUT END CAP | 1-5/8" | B5- COND RACK | 201
STRUT |  | 241000181 |  | 1-5/8" x 1-5/8" SLOTTED STRUT | 1-5/8" X 1-5/8" | B5-COND RK
STRUT | 50110798 |  |  | 1-5/8" x 1-5/8" SLOTTED STRUT MULTI HOLE | 1-5/8" x 1-5/8 | B5- COND RACK
STRUT | 50110801 |  |  | 1-5/8" x 1-5/8" SOLID STRUT | 1-5/8" x 1-5/8 | B5- COND RACK
STRUT | 50110803 |  | UNIT STRUT GREEN PAITED STEEL | 1-5/8" X 1-5/8" UNISTRUT GREEN PAINTED STEEL | 1-5/8" | B5- COND RACK
STRUT | 50110200 |  |  | 1-5/8" x 3-1/4" PLASTIC STRUT END CAP BLACK | 1-5/8" x 3-1/4" | EC4-4 |  |  | MCMASTER P/N 3312T74
STRUT |  | 241000180 |  | 1-5/8" X 3-1/4" SLOTTED UNISTRUT GREEN PAINTED | 1-5/8" X 3-1/4" | B5-COND RK
STRUT | 50110808 |  | UNIT STRUT GREEN PAITED STEEL | 1-5/8" X 3-1/4" SOLID UNISTRUT GREEN PAINTED STEEL | 1-5/8" | B5- COND RACK |  |  | INACTIVE
STRUT |  | 241000359 |  | 1-5/8" x 7/8" SOLID 316 STAINLESS STEEL UNISTRUT 10' LENGTH |  |  |  |  | MCMASTER P/N 33085T96
CABLE |  | 241000334 |  | 16-2 SINGLE PAIR SHLD CABLE 600 VOLTS | 16-2 COND
CABLE |  | 241000333 |  | 16-6 600 VOLT UN-SHLD CABLE | 16-6 COND
CABLE | 50110232 |  | BELDEN 3089A 18/1 TRI THHN-600V BK. | 18 AWG 1 PAIR TRI THHN-600V / RED/BLK/WHT | 18 AWG | B5- COND RACK |  |  | INACTIVE
CABLE |  | 240000122 | 18 AWG 600V 1 PAIR SHIELDED CABLE | 18-2 SINGLE PAIR SHLD CABLE 600 VOLTS | 18 AWG | WIRE RACK
TERMFITT | 40260077 |  | MOLEX 2 SCREW 12 CIRCUIT TERMFITTINAL STRIP | 2 SCREW 12 CIRCUIT TERM STRIP | MISC | EC4-3 | 729
CABLE |  | 241000313 |  | 2 X 20 AWG SINGLE PAIR SHLD CABLE 300 VOLTS | 20 AWG | WIRE RACK |  |  | LAPP 302002S
KOSEAL |  | 241000261 |  | 2" 3 PIECE KNOWCKOUT SEAL, CARBON STEEL | 2" | WIRE RACK
CONDFITT |  | 241000326 |  | 2" 90 DEGREE EMT ELBOWS | 2" | PALLET
HEATSHNK |  | 241000343 |  | 2" BLACK HEAT SHRINK (1-1/4" O.D 2" FLAT) | 2" |  |  |  | MIL-I-23053/5-0, B2 1-1/4" Black, 200'/Spool
NIPPLE |  | 241000257 |  | 2" CHASE NIPPLE | 2" | ORDERED PER JOB
CONDFITT |  | 241000327 |  | 2" EMT 45 DEGREE ELBOWS | 2" | PALLET
CONDFITT |  | 241000325 |  | 2" EMT COM CONNECTORS | 2" | EC4-5
CONDFITT |  | 241000324 |  | 2" EMT COMP COUPLINGS | 2" | EC4-5
CONDUIT |  | 241000323 |  | 2" EMT CONDUIT | 2" | PIPE RACK
CONDFITT |  | 241000270 |  | 2" ERICKSON FEMALE / FEMALE UNION HAZARDOUS LOCATION | 2" | EC4-5
NIPPLE |  | 241000202 |  | 2" GRC CLOSE NIPPLE | 2" CLOSE | EC1-1 | 11 |  | NEED LABEL
CONDUIT |  | 241000182 |  | 2" GRC CONDUIT | 2" | B5-COND RK
CONDFITT |  | 241000079 |  | 2" GRC THREADED COUPLING | 2" | EC1-1 | 22
CONDUIT | 66600407 |  |  | 2" LIQ TIGHT FLEX | 2" | JOB
CONDFITT |  | 241000084 |  | 2" LIQ-TIGHT 45 DEG CONN | 2" | EC2-1 | 6 |  | DESCRIPTION CHANGE
CONDFITT |  | 241000085 |  | 2" LIQ-TIGHT 90 DEG CONN | 2" | EC2-1
CONDFITT |  | 241000083 |  | 2" LIQ-TIGHT STRAIGHT CONN | 2" | EC2-1 | 9
CONDFITT |  | 241000258 |  | 2" LOCKNUT | 2" | ORDERED PER JOB
CONDBODY |  | 241000073 |  | 2" MALL C COND BODY | 2" | EC1-1 | 2
CONDBODY |  | 241000092 |  | 2" MALL COND BODY COVER / FM7 | 2" | EC1-1 | 25 |  | DESCRIPTION CHANGE / NEED LABEL
CONDBODY |  | 241000075 |  | 2" MALL COND BODY COVERS / SCREW TYPE | 2" | EC1-1 | 10 |  | DESCRIPTION CHANGE / NEED LABEL
CONDBODY |  | 241000093 |  | 2" MALL COND BODY GASKET / FM7 | 2" | EC1-1 | 30 |  | DESCRIPTION CHANGE / NEED LABEL
CONDBODY |  | 241000076 |  | 2" MALL COND BODY GASKET / SCREW TYPE | 2" | EC1-1 | 9 |  | DESCRIPTION CHANGE / NEED LABEL
CONDBODY |  | 241000198 |  | 2" MALL LB CONDUIT BODY | 2" | EC1-1
CONDBODY |  | 241000197 |  | 2" MALL LL CONDUIT BODY | 2" | EC1-5
CONDBODY |  | 241000101 |  | 2" MALL LR COND BODY | 2" | EC1-1 | 2
CONDFITT |  | 241000064 |  | 2" MALL RA CLAMP | 2" | EC1-1
CONDFITT |  | 241000175 |  | 2" MALL SEAL OFF FITTING EYS | 2" | EC1-1
CONDBODY |  | 241000071 |  | 2" MALL T COND BODY | 2" | EC1-1 | 10
CONDBODY |  | 241000072 |  | 2" MALL TB COND BODY | 2" | EC1-1 | 1
CONDBODY |  | 241000100 | SPARE | 2" MALL X COND BODY | 2" | EC1-1
CONDFITT |  | 241000082 |  | 2" MEYERS HUB | 2" | EC2-1 | 2
BUSHING |  | 241000259 |  | 2" PLASTIC BUSHING | 2" | ORDERED PER JOB
CHANNEL TRAY |  | 241000358 |  | 2" PLASTIC PROTECTIVE BUSHING FOR CHANNEL TRAY
CONDFITT |  | 241000038 |  | 2" RA COND CLAMPS | 2" | EC1-1 | 16
CONDFITT |  | 241000016 |  | 2" REC HOLE PLUG | 2" | EC2-1 | 21
CONDFITT |  | 241000074 |  | 2" REC PLUGS | 2" | EC1-1
CONDFITT |  | 241000286 |  | 2" STRUT STRAPS / EMT | 2" | EC-3
BUSHING |  | 241000078 |  | 2" X 1" RE BUSHING | 2" | EC1-1 | 90
BUSHING |  | 241000195 |  | 2" X 1" REDUCING BUSHING | 2" x 1" | EC1-4 | 40 |  | NEED LABEL
BUSHING |  | 241000013 |  | 2" X 1/2" RE BUSHING / CORRECT PART NUMBER | 2" | EC2-3 | 8
BUSHING |  | 241000081 |  | 2" X 1/2" RE BUSHING / INACTIVE | 2" | EC2-1 | EC2-1 |  | INACTIVE 10/06/25
BUSHING |  | 241000077 |  | 2" X 1-1/2" RE BUSHING | 2" | EC1-1 | 0
CONDFITT |  | 241000044 |  | 2" X 1-1/4" RE BUSHING | 2" | EC1-1
BUSHING |  | 241000200 |  | 2" X 1-1/4" RE BUSHING | 2" X 1-1/4" | EC1-3
TERMFITT |  | 241000098 |  | 2" X 2" X 1/4" X 3/8" GROUND TAB | 2" | EC5-4
BUSHING |  | 241000194 |  | 2" X 3/4" REDUCING BUSHING | 2" X 3/4"" | EC1-4 | 45 |  | NEED LABEL
CHANNEL TRAY |  | 241000357 |  | 2" x 4" ALUMINUM CHANNEL TRAY
CHANNEL TRAY |  | 241000354 |  | 2" x 4" ALUMINUM CHANNEL TRAY BLIND END PLATE
CHANNEL TRAY |  | 241000356 |  | 2" x 4" ALUMINUM CHANNEL TRAY COVER STRAP / 2 PIECES PER ASSEMBLY
CHANNEL TRAY |  | 241000355 |  | 2" x 4" ALUMINUM CHANNEL TRAY FLANGED SOLID COVER
NIPPLE |  | 241000262 |  | 2-1/2" CHASE NIPPLE | 2-1/2" | ORDERED PER JOB
CONDFITT |  | 241000239 |  | 2-1/2" GALV RIGID ELBOW 90 DEG | 2-1/2" | EC7-1
CONDUIT |  | 241000243 |  | 2-1/2" GRC CONDUIT | 2-1/2" | B5-COND RACK
CONDUIT |  | 241000244 |  | 2-1/2" LIQ-TIGHT FLEX | 2-1/2" | GREENLEE BOX
CONDBODY |  | 241000236 |  | 2-1/2" MALL COND BODY COVER | 2-1/2" | EC7-1
CONDBODY |  | 241000237 |  | 2-1/2" MALL COND BODY GASKET | 2-1/2" | EC7-1
CONDBODY |  | 241000235 |  | 2-1/2" MALL LB COND BODY | 2-1/2" | EC7-1
CONDFITT |  | 241000238 |  | 2-1/2" MEYERS HUB | 2-1/2" | EC7-1
KOSEAL |  | 241000307 |  | 2-1/2" NEMA 1 K.O. SEAL (3PC) | 2-1/2" | need bin location
KOSEAL |  | 241000306 |  | 2-1/2" NEMA 4 K.O. SEAL (3PC) | 2-1/2" | need bin location
BUSHING |  | 241000264 |  | 2-1/2" PLASTIC BUSHING | 2-1/2" | ORDERED PER JOB
CONDFITT |  | 241000242 |  | 2-1/2" RA COND CLAMPS | 2-1/2" | EC7-1
CONDFITT |  | 241000287 |  | 2-1/2" STRUT STRAPS / EMT | 2-1/2" | EC-3
CONDFITT |  | 241000241 |  | 2-1/2” LIQ-TIGHT STRAIGHT CONN | 2-1/2" | EC7-1
CONDFITT |  | 241000240 |  | 2-1/2” THREADED COUPLING | 2-1/2" | EC7-1
CONDFITT |  | 241000263 |  | 2-1-2" LOCKNUT | 2-1/2" | ORDERED PER JOB
CONDFITT |  | 241000173 |  | 3" 45 DEG LIQ TIGHT ELBOW | 3" | JOB | 5 |  | NEED LABEL
CONDFITT | 66600334 |  |  | 3" CLOSE NIPPLE | 3" | JOB
CONDFITT | 66600331 |  |  | 3" EYF MALL SEAL OFF HORIZ / VERTICLE | 3" | JOB
CONDFITT |  | 241000169 |  | 3" GALV RIGID ELBOW 90 DEG | 3" | JOB
CONDFITT | 66600334 |  |  | 3" GRC CLOSE NIPPLE | 3" | JOB
CONDUIT |  | 241000174 |  | 3" GRC CONDUIT | 3" | JOB
CONDFITT |  | 241000080 |  | 3" GRC THREADED COUPLING | 3" | EC1-1 | 6
CONDUIT | 66600328 |  |  | 3" LIQ TIGHT FLEX | 3" | JOB
CONDFITT | 666000329 |  |  | 3" LIQ TIGHT STRAIGHT CONNECTOR | 3" | EC2-1 |  |  | INACTIVE
CONDBODY |  | 241000067 |  | 3" MALL COND BODY COVER | 3" | EC1-1 | 3
CONDBODY |  | 241000068 |  | 3" MALL COND BODY GASKET | 3" | EC1-1 | 6
CONDBODY |  | 241000066 |  | 3" MALL LB COND BODY | 3" | EC1-1
CONDFITT |  | 241000065 |  | 3" MALL RA CLAMP | 3" | EC1-1 | 10
CONDFITT |  | 241000171 |  | 3" MEYERS HUB | 3" | JOB
CONDFITT |  | 241000177 |  | 3" RIDGID THREADED COUPLING | 3" | JOB
CONDFITT |  | 241000172 |  | 3" STRAIGHT LIQ TIGHT CONNECTOR | 3" | JOB | 4
CONDFITT |  | 241000288 |  | 3" STRUT STRAPS / EMT | 3" | EC-3
BUSHING |  | 241000216 |  | 3" X 1-1/4" REDUCING BUSHING | 3" X 1-1/4" | EC1-1 | 2 |  | NEW PART NUMBER / LABEL
BUSHING |  | 241000069 |  | 3" X 2" RE BUSHING | 3" | EC1-1 | 10
MISC |  | 241000300 |  | 3" X 4" x 3/8" DESSICANT BAGS | 3" X 4" | ELECTRICAL CABINET
HEATSHNK |  | 241000329 |  | 3/16" GREEN / YELLOW HEAT SHRINK | 5/16" | ELECTRICAL CABINET
HEATSHNK | 53460145 |  | ORANGE HEAT SHRINK TUBING | 3/16" ORANGE HEAT SHRINK TUBING | 0.125" | CABINET
CONDFITT | 50112048 |  | CROUSE-HINDS VER./HOR. M/F SEAL CONDFITT | 3/4" MALL SEAL OFF COND FITT EYS | 3/4" | EC2-2 | 17 |  | NEED LABEL
KOSEAL |  | 241000018 |  | 3/4" 3 PIECE K.O. SEAL TYPE 1 | 3/4" | EC4-4 | 88
TAPE |  | 241000019 |  | 3/4" 3M GREEN 35 ELECTRIC TAPE | 3/4" | EC5-2 | 8
CONDFITT |  | 241000094 |  | 3/4" 90 DEG. PULL ELB MALE / FEM NON HAZ LOC | 3/4" | EC1-2 | 36
CONDFITT | 50110079 |  |  | 3/4" CHASE NIPPLE | 3/4" | OBSOLETE
CONDBODY |  | 241000223 |  | 3/4" COND BODY COVER FM7 | 3/4" | EC1-2 | 1 |  | NEW PART NUMBER / LABEL
CONDBODY |  | 241000221 |  | 3/4" COND BODY GASKET / FM7 | 3/4" | EC1-2 | 18 |  | NEW PART NUMBER / LABEL
CONDBODY |  | 241000222 |  | 3/4" COND BODY GASKET SCREW TYPE | 3/4" | EC1-2 | 25 |  | NEW PART NUMBER / LABEL
CONDBODY | 35000033 | INCATIVE | 3/4 " CONDBODY COVER GASKET CROUSE HINDS GK75N | 3/4" CONDBODY COVER COVER / INACTIVE | 3/4" | EC1-2 |  | 7 | INACTIVE 10/07/25
CORDGRIP | 49360024 |  | SEALCON 3/4" NPT 2 HOLE .31" CORDGRIP | 3/4" CORDGRIP 2 HOLES 0.31" | 3/4" | EC4-3 | 133
CONDFITT |  | 241000117 |  | 3/4" DRAIN BREATHER | 3/4" | EC1-3 | 87
CONDFITT |  | 241000049 |  | 3/4" FEM / FEM 45 DEG SHORT ELB HAZ LOC | 3/4" | EC2-2 | 6
CONDFITT |  | 241000048 |  | 3/4" FEM / FEM 90 DEG SHORT ELB HAZ LOC | 3/4" | EC2-2 | 10
NIPPLE | 50110051 |  | 3/4" X CLOSE COND NIPPLE | 3/4" GRC CLOSE NIPPLE | 3/4" | EC1-2 | 23
CONDUIT | 50110114 |  | RIGID GALVANIZED COND | 3/4" GRC CONDUIT | 3/4" | B5- COND RACK
CONDFITT | 50110187 |  | 3/4" EMT STRUT STRAPS | 3/4" GRC STRUT STRAPS | 3/4" | EC1-2
CONDFITT |  | 241000217 |  | 3/4" GRC THREADED COUPING | 3/4" | EC1-2 | 49 |  | NEW PART NUMBER / LABEL
CONDBODY |  | 241000045 |  | 3/4" GRL AL COND BODY HAZ LOC | 3/4" | EC1-2 | 4
CONDFITT | 30304202 |  | HOFFMAN HOLE PLUG | 3/4" HOFFMAN HOLE PLUG 3 PIECE TYPE 4 | 3/4" | EC4-4 | 104
CONDBODY |  | 241000047 |  | 3/4" LBY FEM / FEM COND BODY HAZ LOC | 3/4" | EC1-2 | 1
CONDFITT |  | 241000219 |  | 3/4" LIQ TIGHT 45 DEGREE ELBOW / | 3/4" | EC2-1 | 6 |  | NEW PART NUMBER / LABEL
CONDFITT |  | 241000353 |  | 3/4" LIQ TIGHT 90 DEG ELBOW / NO GROUND | 3/4"
CONDFITT |  | 241000352 |  | 3/4" LIQ TIGHT STRAIGHT CONN / NO GROUND | 3/4"
CONDFITT | 50112252 |  | CROUSE-HINDS METALIC SEALTIGHT 45 DEG. | 3/4" LIQ-TIGHT 45 DEG CONN / GROUND | 3/4" | EC2-2 | 11 |  | DESCRIPTION CHANGE
CONDFITT | 50112256 |  | CROUSE-HINDS METALIC SEALTIGHT 90 DEG. | 3/4" LIQ-TIGHT 90 DEG CONN / WITH GROUND | 3/4" | EC2-2 | 32 |  | DESCRIPTION CHANGE
CONDUIT | 50112268 |  | 3/4" FLEX COND METALLIC **MUST BE UL LISTED** | 3/4" LIQ-TIGHT FLEX COND | 3/4" | GREENLEE BOX
CONDFITT | 50112264 |  | LIQTIGHT SEAL RING ASSY. T & B | 3/4" LIQ-TIGHT SEAL RING | 3/4" | EC4-4 | 794
CONDFITT | 50112260 |  | CROUSE-HINDS METALIC STRAIGHT CONN. | 3/4" LIQ-TIGHT STRAIGHT CONN / GROUND | 3/4" | EC2-2 | 77 |  | DESCRIPTION CHANGE TWO BIN LOCATION
CONDFITT | 50110116 |  | LOCK RING | 3/4" LOCK RING | 3/4" | EC4-4 | 517
CONDFITT | 50112244 |  |  | 3/4" MALE / FEM 90 DEG SHORT ELB HAZ LOC | 3/4" | EC2-2 | 50
CONDBODY |  | 241000116 |  | 3/4" MALL C COND BODY | 3/4" | EC2-3 | 14 | 4
CONDBODY | 50112204 |  | 3/4" MALL CONDBODY COVER CROUSE-HINDS K75M | 3/4" MALL COND BODY COVER / SCREW TYPE | 3/4" | EC2-2 | 8 |  | DESCRIPTION CHANGE
CONDBODY |  | 241000187 |  | 3/4" MALL LB COND BODY | 3/4" | EC1-2 | 0 | 12
CONDBODY |  | 241000186 |  | 3/4" MALL LL COND BODY | 3/4" | EC1-2 | 10 | 13
CONDBODY |  | 241000046 |  | 3/4" MALL LR COND BODY | 3/4" | EC1-2 | 10 | 15 | TWO SEPARATE BINS
CONDFITT | 50110020 |  |  | 3/4" MALL RA CLAMP | 3/4" | EC1-2 |  |  | DUPLICATE PART
CONDBODY | 50111404 |  | CRHI T75M 3/4" MALL "T" CONDBODY | 3/4" MALL T COND BODY | 3/4" | EC1-2 | 4 | 8
CONDBODY | 50112229 |  | CROUSE-HINDS MALL TB CONDBODY | 3/4" MALL TB COND BODY | 3/4" | EC1-2 | 0 | 4 | TWO SEPARATE BINS
CONDFITT |  | 241000109 |  | 3/4" MALL UNION 90 HAZ LOC UNL | 3/4" | EC2-2 | 12
CONDFITT | 50112048 |  |  | 3/4" MALL VERT / HORIZ SEAL COND FITT | 3/4" | EC1-2 | 17
CONDBODY | 50112205 |  | CROUSE- HINDS MALL X CONDBODY | 3/4" MALL X COND BODY | 3/4" | EC1-2 | 25 | 10 | TWO SEPARATE BINS
CONDFITT | 50110860 |  | CROUSE-HINDS MEYERS HUB (GROUND) | 3/4" MEYERS HUB | 3/4" | EC2-2 | 12 | 23
CORDGRIP |  | 241000339 |  | 3/4" NPT BLACK NYLON CORD GRIP (.35-.63) | 3/4" |  |  |  | SEALCON P/N CD21NR-BK
CORDGRIP |  | 241000338 |  | 3/4" NPT O-RING | 3/4"
KOSEAL |  | 241000039 |  | 3/4" NPT PLASTIC HOLE PLUG | 3/4" | EC4-4 | 196
CORDGRIP |  | 241000337 |  | 3/4" NPT PLASTIC LOCKNUT | 3/4"
BUSHING |  | 241000271 |  | 3/4" PLASTIC BUSHING | 3/4" | EC2-5
CONDSUPP | 50110184 |  | 3/4" COND CLAMP # RAC75HD | 3/4" RA COND CLAMPS | 3/4" | EC3-1 | 84
CONDFITT |  | 241000011 |  | 3/4" REC HOLE PLUG | 3/4" | EC2-2 | 43
SPLITUBE |  | 241000320 |  | 3/4" SPLIT TUBING BLACK 100'/ ROLL | 3/4" | ELECTRICAL CABINET
CONDFITT |  | 241000283 |  | 3/4" STRUT STRAPS / EMP | 3/4" | EC-3
CONDFITT | 50110071 |  | RED WASHER | 3/4" TO 1/2" RED WASHER | 3/4" | EC5-4
CONDFITT | 50112240 |  | CROUSE-HINDS STEEL UNION | 3/4" UNION MALE / FEM UNY | 3/4" | EC1-2 | 27
BUSHING | 50110131 | WAS 50110139 | 3/4" X 1/2" RE BUSHING / INACTIVE | 3/4" X 1/2" RE BUSHING | EC4-3
BUSHING | 50110139 |  | CROUSE-HINDS 3/4"- 1/2" NPT RE BUSHING CLASS 1 DIV 11 (RE21) | 3/4" X 1/2" RE BUSHING / INACTIVE | 3/4" | EC4-3 | 319 |  | INACTIVE
CONDFITT |  | 241000058 |  | 3/4" X 1/2" RED WASHERS | 3/4" | EC5-4 | 295
NIPPLE |  | 241000220 |  | 3/4" X 2" GRC NIPPLE | 3/4" | EC1-1 | 25 |  | NEW PART NUMBER / LABEL
NIPPLE | 50110310 |  | 3/4" X 3" COND NIPPLE | 3/4" X 3" GRC NIPPLE | 3/4" | EC1-2 | 19
NIPPLE | 50110311 |  | 3/4" X 4" COND NIPPLE | 3/4" X 4" GRC NIPPLE | 3/4" | EC1-2 | 11
NIPPLE | 50110312 |  |  | 3/4" X 5" GRC NIPPLE | 3/4" | OBSOLETE
NIPPLE | 50110313 |  |  | 3/4" X 6" GRC NIPPLE | 3/4" | OBSOLETE
CONDFITT |  | 241000314 |  | 3/4"" ERICKSON FEMALE / FEMALE UNION NON HAZARDOUS | 3/4" | EC2-2
FASTENER |  | 241000207 |  | 3/8 -18 X 2" x 3/4" X 1-1/8" CORROSION RESISTANT VIBRATION DAMPING SANDWICH MOUNT #5823K21 | 2" | EC6-3 |  |  | McMaster P/N 5823K21
HEATSHNK | 40804410 |  | BLACK HEAT SHRINK TUBING | 3/8" BLACK HEAT SHRINK TUBING | 3/8" | CABINET |  |  | INACTIVE
NEXT AVAILABLE |  | 241000367 |  | 3/8" BLUE HEAT SHRINK |  | EC-CABINET
FASTENER |  | 241000032 |  | 3/8" FENDER WASHER SS | 3/8" | EC5-3 | 7
FASTENER |  | 241000033 |  | 3/8" FLAT WASHER SS (100 PER BOX) | 3/8" | EC5-3 | 318 |  | MCMASTER P/N 92141A031 (100 / PACK)
FASTENER |  | 241000037 |  | 3/8" HEX NUTS SS | 3/8" | EC5-3 | 82 |  | MCMASTER P/N 92141A031 (100 / PACK)
FASTENER |  | 241000061 |  | 3/8" RUBBER SEALING WASHER | 3/8" | EC5-3 | 35
FASTENER |  | 241000031 |  | 3/8" SPLIT LOCK WASHER SS | 3/8" | EC5-3 | 317 |  | MCMASTER P/N 92146A031 (100 / PACK)
SPLITUBE |  | 241000191 |  | 3/8" SPLIT TUBING BLACK 100' / ROLL | 3/8" | EC-CAB
FASTENER |  | 241000035 |  | 3/8" X 1" HEX HEAD CAP SCREW SS | 3/8" | EC1-2 | 306
NEXT AVAIL |  | 241000340 |  | 3/8" X 1/4" SQUARE WASHERS PLATED STEEL | N/A
FASTENER |  | 241000150 |  | 3/8" X 1-1/2" HEX HEAD CAP SCREW SS | 3/8" | EC5-3 | 91
FASTENER |  | 241000036 |  | 3/8" X 1-1/4" HEX HEAD CAP SCREW SS | 3/8" | EC5-3 | 116 |  | MCMASTER P/N 92314A544 ( 25 / PACK)
STRUT |  | 241000360 |  | 3/8" X 13-16" 316 STAINLESS STEEL SPRING NUT |  |  |  |  | MCMASTER P/N 3259T27
FASTENER |  | 241000188 |  | 3/8" X 2" HEX HEAD CAP SCREW SS 18-8 | 3/8" X 2" | EC5-3 | 113 |  | MCMASTER P/N 92240A632
FASTENER |  | 241000034 |  | 3/8" X 3/4" HEX HEAD CAP SCREW SS | 3/8" | EC5-3 | 207
HARDWARE |  | 241000361 |  | 3/8"-16 X 5/8" 316 STAINLESS STEEL HEX HEAD SCREW |  |  |  |  | MCMASTER P/N 93190A621
CONDFITT |  | 241000289 |  | 3-1/2" STRUT STRAPS | 3-1/2" | EC-3
STRUT | 50110314 |  | 3-1/4"x1-5/8"X20' GREEN PAINTED SOLID STRUT CHANNEL | 3-1/4" X 1-5/8" X 20' GREEN PAINTED SOLID STRUT CHANNEL | 3-1/4" | B5- COND RACK
TAPE | 50110034 |  |  | 3M BLACK 33+ ELECTRICAL TAPE | N/A | EC5-2 | 17 |  | DUPLICATE
TAPE | 66600239 |  |  | 3M BLUE 35 CODING TAPE | N/A | EC5-2
TAPE | 66600228 |  |  | 3M BROWN 35 CODING TAPE | N/A | EC5-2
TAPE | 66600233 |  |  | 3M GREEN 35 CODING TAPE | N/A | EC5-2
TAPE | 66600231 |  |  | 3M ORANGE 35 CODING TAPE | N/A | EC5-2
TAPE | 66600362 |  |  | 3M RED 35 CODING TAPE | N/A | EC5-2
TAPE | 50115001 |  |  | 3M RUBBER SPLICING TAPE SCOTCH 3/4" 130C | N/A | EC5-2 | 11
TAPE | 50115000 |  |  | 3M VARNISHED CABRICK TAPE WITH ADHESIVE SCOTCH 2520 | N/A | EC5-2 | 17
TAPE | 66600221 |  |  | 3M WHITE 35 CODING TAPE | N/A | EC5-2 | 1
TAPE | 66600232 |  |  | 3M YELLOW 35 CODING TAPE | N/A | EC5-2 | 4
CONDFITT |  | 241000154 |  | 4" 45 DEG LIQ TIGHT ELBOW | 4" | JOB
CONDFITT |  | 241000298 |  | 4" CHASE NIPPLE | 4" | TO JOB NO STOCK
NIPPLE |  | 241000347 |  | 4" CLOSE NIPPLE
CONDFITT |  | 241000294 |  | 4" EMT 45 DEGREE ELBOW | 4" | TO JOB NO STOCK
CONDFITT |  | 241000293 |  | 4" EMT 90 DEGREE ELBOW | 4" | TO JOB NO STOCK
CONDFITT |  | 241000296 |  | 4" EMT COMPRESSION CONNECTOR | 4" | TO JOB NO STOCK
CONDFITT |  | 241000292 |  | 4" EMT COMPRESSION COUPLING | 4" | TO JOB NO STOCK
CONDUIT |  | 241000276 |  | 4" EMT CONDUIT | 4" | B5-COND RACK
CONDFITT |  | 241000277 |  | 4" EMT CONNECTOR COMPRESSION | 4" | EC-3
CONDFITT |  | 241000151 |  | 4" GALV RIGID ELBOW 90 DEG | 4" | JOB
CONDUIT |  | 241000163 |  | 4" GRC CONDUIT | 4" | JOB
CONDFITT |  | 241000297 |  | 4" GROUNDING BUSHING | 4" | TO JOB NO STOCK
CONDFITT |  | 241000279 |  | 4" GROUNDING LOCKNUT | 4" | EC-3
CONDFITT |  | 241000295 |  | 4" IP RATED SEALING RINGS | 4" | TO JOB NO STOCK
CONDBODY |  | 241000291 |  | 4" LB MOGUL PULLING FITTING | 4" | TO JOB NO STOCK
CONDFITT |  | 241000308 | 241000308 | 4" LIQ TIGHT 90 DEGREE ELBOW | 4" | need bin location
CONDUIT |  | 241000159 |  | 4" LIQ TIGHT FLEX | 4" | JOB
CONDFITT |  | 241000281 |  | 4" LOCK RING | 4" | EC-3
CONDFITT |  | 241000153 |  | 4" MEYERS HUB | 4" | JOB
CONDFITT |  | 241000299 |  | 4" PLASTIC BUSHING | 4" | TO JOB NO STOCK
CONDFITT |  | 241000158 |  | 4" RA CLAMPS | 4" | JOB
CONDFITT |  | 241000280 |  | 4" SEALING RING | 4" | EC-3
CONDFITT |  | 241000155 |  | 4" STRAIGHT LIQ TIGHT CONNECTOR | 4" | JOB
CONDFITT |  | 241000290 |  | 4" STRUT STRAPS / EMT | 4" | EC-3
CONDFITT |  | 241000157 |  | 4" THREADED COUPLING | 4" | JOB
BUSHING |  | 241000070 |  | 4" X 3" RE BUSHING | 4" X 3" | EC1-1 | 3
FASTENER |  | 241000029 |  | 5/16" NYLON INSERT HEX LOCKNUT SS | 5/16" | EC5-3 | 733
FASTENER | 51000502 |  | 5/16" NYLON INSERTS LOCKNUT PLATED | 5/16" NYLON INSERT HEX LOCKNUT SS | 5/16" | EC5-3
FASTENER |  | 241000027 |  | 5/16" FLAT WASHER SS | 5/16" | EC5-3 | 415
FASTENER |  | 241000104 |  | 5/16" HEX NUTS SS | 5/16" | EC5-3 | 246
FASTENER |  | 241000030 |  | 5/16" SPLIT LOCK WASHER SS | 5/16" | EC5-3 | 346 |  | MCMASTER P/N 92146A030 (100 / PACK)
FASTENER | 51000108 |  | 5/16" LOCKWASHER PLATED | 5/16" SPLIT LOCK WASHER SS | 5/16" | EC5-3
FASTENER |  | 241000026 |  | 5/16" X 1" HEX HEAD CAP SCREW SS | 5/16" | EC5-3 | 464
FASTENER | 50110063 |  | MALE / FEM VIBRATION ISOLATOR | 5/16"-18 VIBRATION ISOLATOR | 5/16" | MOVE TO CAGE AREA
FASTENER |  | 241000062 |  | 5/16"-18 X 1" HEX HEAD CAP SCREW SS | 5/16" | EC5-3
FASTENER |  | 241000028 |  | 5/16"-18 X 3/4" HEX HEAD CAP SCREW SS | 5/16" | EC5-3 | 81 |  | MCMASTER P/N 92240A581 (50 / PACK)
FASTENER | 51000190 |  | 5/16" 18 X 3/4" HEX CAP SCREW | 5/16"-18 X 3/4" HEX HEAD CAP SCREW SS | 5/16" | EC5-3
CONSM | 60000354 |  |  | 567 LOCTITE THREAD SEALANT | N/A | EC4-2
TERMFITT | 66600372 |  |  | 8-32 GROUND SCREW | 8-32 | EC5-3
FERRULES |  | 241000226 |  | AW10012 - 18 AWG (12mm PIN) ISNULATED FERRULES | 18 AWG | EC5-3 | 500 |  | NEW PART NUMBER / LABEL
HEATSHNK | 53460143 |  |  | BLACK HEAT SHRINK .19 ID | .19 ID | EC-CABINET
TERMFITT |  | 241000318 |  | BLUE HEAT SHRINK .19" (3/16") | .19" | ELECTRICAL CABINET |  |  | MCMASTER P/N #7856K44
TERMFITT | 50110260 |  | SMALL BLUE WIRE NUTS | BLUE WIRE NUTS #22 AWG - #16 AWG | 22-16 AWG | EC5-4 | 179
ZIPTIES | 50110068 |  | CABLE TIE 11 3/4" l-11-50-O-C **BLACK** | CABLE TIE 11" BLACK | 11" | CABINET
ZIPTIES |  | 241000304 |  | CABLE TIE 14.10" (L) X.29" (W) HD BLACK | 14.10" X.29" | ELECTRICAL CABINET |  |  | P/N 4014ST
NEXT AVAILABLE |  | 241000365 |  | CHANNEL TRAY BONDING JUMPER 600 AMPS |  |  |  |  | BLINE 99-N1
CONSM | 50991430 |  | COLD/GALVANIZED SPRAY | COLD/GALVANIZED SPRAY | MISC | CABINET
CONDBODY |  | 241000345 |  | CONDUIT BODY GASKET 4"
DINCABLE | 66600528 |  |  | CRDST VALVE 4A 110-220V 3X18 AWG (SOLENOID VALVES) | #18 AWG | MOVE TO 400 CAGE AREA
WIRE |  | 241000350 |  | EPDM #2/0 AWG 600 VOLT CABLE HIGH FLEXIBLILTY | #2/0 |  |  |  | McMaster P/N 6948K96
FLAT BAR |  | 241000364 |  | FLAT BAR, 316 STAINLESS STEEL, 1" X 1/8" X 10'
HARDWARE |  | 241000348 |  | FLAT WASHER,3/4", SS
TERMFITT | 49456028 |  | FORK TERMFITTINAL 16-14 AWG WIRE MCMASTER CARR P/N: 69145K74 | FORK TERMFITTINAL 16-14 AWG WIRE / BLUE | 16-14 AWG | EC5-4 | 128
TERMFITT | 49456007 |  | FORK TERMFITTINAL 18-14 AWG WIRE | FORK TERMFITTINAL 18-14 AWG WIRE / RED | 18-14 AWG | EC5-4
CONSM |  | 241000189 |  | IDEAL 30-030 NOALOX 8 OS BOTTLE | 8 OZ | EC-CAB
CONSM |  | 241000192 |  | IDEAL 31-388 Clear Gli | 1 QT | EC-CAB
CONSUM |  | 241000319 |  | INACTIVE PART NUMBER 09_22_25 | N/A | ELECTRICAL CABINET |  |  | 31-338
CABLE |  | 241000309 |  | LAPP-25 COND / 18 AWG 600 VOLT / MOTOR RTD CABLE | 18 AWG | WIRE RACK |  |  | LAPP P/N 60185
CLAMPS |  | 241000099 |  | LOOM CLAMPS I.D. 1.0" | 1" | EC5-4 | 51
CLAMPS |  | 241000055 |  | LOOM CLAMPS I.D. 1/2" | 1/2" | EC5-4 | 269
CLAMPS |  | 241000056 |  | LOOM CLAMPS I.D. 5/8" | 5/8" | EC5-4 | 179
CLAMPS |  | 241000057 |  | LOOM CLAMPS I.D. 7/8" | 7/8" | EC5-4 | 68
BUSHING |  | 241000248 |  | M20 X 3/4" NPT ADAPTOR NICKEL PLATED | M20 X 3/4" | EC1-2
FASTENER |  | 241000205 |  | M8 METRIC OVERSIZED WASHER | M8 | EC6-3 |  |  | McMaster P/N 93849A202
FASTENER |  | 241000206 |  | M8 METRIC SPLIT WASHER PACK OF 100 / EACH | M8 | EC6-3 |  |  | McMaster P/N 92146A545
FASTENER |  | 241000204 |  | M8 SS METRIC WASHER PACK OF 100 / EACH | M8 | EC6-3 |  |  | McMaster P/N 98689A116
FASTENER |  | 241000203 |  | M8 X 1"x 1" x 3/4" CORROSION RESISTANT VIBRATION DAMPING SANDWICH MOUNT | M8 | EC6-3 |  |  | McMaster P/N 5823K43
FASTENER |  | 241000301 |  | M8 X 1.25 mm STAINLESS HEX NUTS | M8 | EC6-3
FASTENER |  | 241000167 |  | MALE / MALE CORROSION RESISTANT VIBRATION DAMPING SANDWICH M8 X 1.25MM | 1" | EL5-1 | 14 |  | MCMASTER P/N 5823K43
FASTENER |  | 241000168 |  | MALE / MALE VIBRATION DAMPING SANDWICH MOUNT 2-1/2" X 3/8"-16-1-1/8" | 2-1/2" | EL5-1 | 6 |  | MCMASTER P/N 9213K74
CONDFITT |  | 241000317 | MECHANICAL LUG #4 - 350 AWG RANGE | MECHANICAL LUG #4 - 350 AWG RANGE | #4 - 350 AWG |  |  |  | BURNK2A31U
CONDFITT |  | 241000346 |  | MEDIUM PRESSURE 303 STAINLESS PIPE ADAPTOR 1/4"-28 FEMALE PIPE FITTING | 1/4-28X3/4" | ORDERED TO JOB |  |  | MCMASTER P/N 2684K333
MYPRO |  | 241000003 | MTA-111-120 | MTA-111-120 | N/A | 455
MYPRO |  | 241000005 | MTA-111-120-S | MTA-111-120-S | N/A | 455
MYPRO |  | 241000006 | MTA-121-120-V1K-S MYPRO TOUCH AD | MTA-121-120-V1K-S | N/A | 455
MYPRO |  | 241000007 | MTA-211-120-V1K-S | MTA-211-120-V1K-S | N/A | 455
MYPRO |  | 241000002 | MYPRO MTA-011-120 | MYPRO MTA-011-120 | N/A | 455
MYPRO |  | 241000001 | MYPRO MTA-011-120-S | MYPRO MTA-011-120-S | N/A | 455
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
NEXT AVAILABLE
CABLE |  | 241000362 |  | OKONITE 16 AWG 1PAIR SHIELDED 600 VOLT CABLE / P/N 264-60-4401 |  |  |  |  | P/N 264-60-4401
CABLE |  | 241000363 |  | OKONITE 16 AWG 1TRIAD SHIELDED 600 VOLT CABLE / P/N 264-65-4401 |  |  |  |  | P/N 264-65-4401
NEXT AVAILABLE |  | 241000368 |  | OLFLEX 18 AWG, 12 CONDUCTOR, 1 GROUND RTD CABLE |  |  |  |  | LAPP CABLE P/N 601812
NEXT AVAILABLE |  | 241000369 |  | OLFLEX 18 AWG, 18 CONDUCTOR, 1 GROUND RTD CABLE |  |  |  |  | LAPP CABLE P/N 601818
TERMFITT | 50110048 |  |  | ORANGE WIRE NUT | N/A | EC-CABINET
FASTENER |  | 241000231 |  | P/N 93635A330 M8 X 35mm X 1.25 / 316 SS SCREW (PACKS OF 5 EACH) |  |  |  |  | P/N 93635A330
FASTENER |  | 241000230 |  | P/N 94205A260 M8 X 1.25mm NYLON INSERT NUTS (PACK OF 25 EACH) |  |  |  |  | P/N 94205A260
FASTENER |  | 241000229 |  | P/N 95211A180 M8 X 8.4 X 24 SS FLAT WASHER (10 PER PACK) |  |  |  |  | P/N 95211A180
TERMFITT |  | 241000267 |  | QUICK DISCONNECT TERMINALS #16 TO #14 AWG .25" STUD 90 DEGREE | 16-14 AWG | ELECTRICAL CABINET
MYPRO |  | 241000004 | RC-100-120 | RC-100-120 | N/A | 455
CONDFITT |  | 241000322 |  | RE BUSHING 3" X 2-1/2" | 3" X 2-1/2"
HEATSHNK | 53460142 |  |  | RED HEAT SHRINK .19 ID | .19 ID | EC-CABINET
TERMFITT | 50110088 |  |  | RED WIRE NUT | N/A | EC-CABINET
TERMFITT | 50110088 |  | RED WIRE NUTS | RED WIRE NUTS #18 AWG -#10 AWG | 18-10 AWG | EC5-4
CONDFITT |  | 241000246 |  | RIGID ELBOW 45 DEG, GALV , 2-1/2" | 2-1/2" | PALLET
ENCLOSURE |  | 241000344 |  | RITTAL WM201608N4 WALL MOUNTED STAINLESS STEEL NEMA 4X, IP 66 WITH MOUNTING PLATE ENCLOSURE |  | ORDERED TO JOB |  |  | WM201608N4
TAPE |  | 241000227 |  | RUBBER MASTIC TAPE #228 2" X 10' | N/A | EC5-2 | 4 |  | NEW PART NUMBER / LABEL
FASTENER |  | 241000225 |  | RUBBER SEALING WASHERS | .275 X .625 | EC5-3 | 222 |  | NEW PART NUMBER / LABEL
TAPE |  | 241000228 |  | SCOTCH SUPER 33+ ELECTRICAL TAPE | 3/4" | EC5-2 | 17 |  | NEW PART NUMBER / LABEL
CORDGRIP |  | 241000142 |  | SEALCON 1/2IN NPT BLACK NYLON LOCKING NUT, NN-12-BK | 1/2″ | EC4-2 | 188
CORDGRIP |  | 241000141 |  | SEALCON 1/2IN NPT BLACK NYLON REDUCED DOME CABLE GLAND, CD13NR-BK | 1/2″ | EC4-2 | 193
CORDGRIP |  | 241000143 |  | SEALCON 1/2IN NPT BUNA-N O-RING, OR-18-BN | 1/2″ | EC4-2 | 224
CORDGRIP |  | 241000145 |  | SEALCON 1IN NPT BLACK NYLON LOCKING NUT, NN-29-BK | 1" | EC4-2 | 327
CORDGRIP |  | 241000144 |  | SEALCON 1IN NPT BLACK NYLON STANDARD DOME MULTI-HOLE, CD29N3-BK | 1" | EC4-2 | 327 |  | PRINT TWO LABELS
CORDGRIP |  | 241000146 |  | SEALCON 1IN NPT BUNA-N O-RING, OR-10-BN | 1" | EC4-2 | 367
TAPE | 50160105 |  |  | TEFLON TAPE 1/2" X 260 FT | 1/2" | EC4-4 | 42
|  | 30002 |  | TERMINAL FITTINGS, SINGLE COMP LUG, #6 AWG, 3/8" STUD |  |  |  |  | MCMASTER CARR P/N 6926K37
WIRE |  | 241000245 |  | THHN 2/0 AWG STRANDED GREEN WIRE | #2/0 AWG | PALLET
STRUT | 50110797 | DELETED | VERTICAL BLACK PLASTIC COVER | UNISTRUT BLACK PLASTIC COVER 10 FT. LENGTH | 1-5/8" | B5- COND RACK
WIRE |  | 241000336 |  | WIRE, #1/0 AWG, THHN, BLACK | 1/0 AWG
CABLE |  | 241000260 |  | WIRE, 18AWG, 1PAIR, TRIAD, 600 VOLTS | 18 AWG | WIRE RACK
TERMFITT | 50110089 |  |  | YELLOW WIRE NUT | N/A | EC-CABINET
``